## Sheet1
Name of the work: Erection of new 33/11kV Outdoor substation with 2x12.5MVA PTRs and also Construction of Control room, and other Civil works at Nallagandla HUDA in Nallagandla section of operation Gachibowli division in cybercity circle, in Master plan Sub-division 1 of WCGH Division in Rangareddy circle under T&D improvement works.
1.SP.O.O.(Projects)Ms.No.1090,Dated:11.07.2024
2. WBS No. S-1798-13-04-01-01-001
Sl.No | Estimate Quantity(Only Figures) | PARTICULARS | Work Type | Item Short Description | SWR No/APSS/Morth cl.No | Rate (INR) (Upto 2 Decimals) | UOM | Amount
1 | 16 | Loading of R.S. Joists 150 x 150mm / Rail poles | Elecy | labour | SWR10205 | 176 | EA | 2816
2 | 5.76 | Transport of iron materials such as R.S. Joists, Rail Poles, fabricated supports, steel, iron, flat, M.S. Channels etc., by lorries. (excluding of loading & unloading ) Above 10 KM and upto 20 KM | Elecy | labour | SWR10132 | 412.08 | TO | 2373.5808
3 | 16 | Un loading of R.S. Joists 150 x 150mm / Rail poles | Elecy | labour | SWR10523 | 107 | EA | 1712
4 | 8 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders) 9.1 Mtrs PSCC Poles 0.76 M x 0.76M x 1.83M (2.6" x 2.6" x 6.0") Exca Hard pit w/o blast 0.76X0.76X1.83M | Elecy | labour | SWR11039 | 928 | EA | 7424
5 | 8 | Excavation of pits in hard rock requiring blasting. (other than SS) 9.1Mtrs PSCC Pole 0.76 M x 0.76M x 1.83M (2.6" x 2.6" x 6.0") EXCAV. OF PIT HARD(2.6" x 2.6" x 6.0") | Elecy | labour | SWR10112 | 1770 | EA | 14160
6 | 5.76 | Fabrication of Main and Auxiliary structures with power drilling using raw steel such as M.S.Angles, Plates, Channels, R.S.Joists, including the supply and fabrication of 6mm base and top plate for Box pole to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection. Fabrication of struc.with power drilling | Elecy | labour | SWR10868 | 6852 | TO | 39467.52
7 | 5.76 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. Sup Material for 1st coat Al. Painting. | Elecy | supply | SMR40009 | 2181 | TO | 12562.56
8 | 5.76 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium Labour for 1st coat Al. Painting. | Elecy | labour | SWR10877 | 851 | TO | 4901.76
9 | 5.76 | Painting of sub-station structures with two coats of Aluminium paint usingAluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2ndcoat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. Sup Material for 2nd coat Al. Painting. | Elecy | supply | SMR40010 | 1293 | TO | 7447.68
10 | 5.76 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium . Labour for 2nd coat Al. Painting. | Elecy | labour | SWR10879 | 482 | TO | 2776.32
11 | 5.76 | Alligning the Main and Auxiliary structures such as RS joist, M.S.Angles, Plates, Channels, Structure to zero level duly leveling in prefabricated MS frames with Hydraulic jacks before galvanising/ fabrication | Elecy | labour | SWR10867 | 1470 | TO | 8467.2
12 | 16 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation. Erection of RS Joist 150 x 150 mm | Elecy | labour | SWR10348 | 1952.61 | EA | 31241.76
13 | 17.758 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Including the cost of cement | Elecy | labour | SWR10356 | 6579 | M3 | 116829.882
14 | 9.24 | Plastering 2 coats, 20/16 mm (1:6)/(1:4) | Elecy | labour | SWR10862 | 373 | M2 | 3446.52
15 | 16 | Painting of poles Paint of coping with 2 coats of white cement incl cost of paints etc. | Elecy | labour | SWR11089 | 48 | EA | 768
16 | 5.063 | Loading of M.S.Channels, Angles, Flats & Rods etc., | Elecy | labour | SWR10206 | 221 | TO | 1118.923
17 | 5.063 | Transport of iron materials such as R.S. Joists, Rail Poles, fabricated supports, steel, iron, flat, M.S. Channels etc., by lorries. (excluding of loading & unloading ) Above 10 KM and upto 20 KM | Elecy | labour | SWR10132 | 412.08 | TO | 2086.361
18 | 5.063 | Un loading of M.S.Channels, Angles, Flats & Rods etc., | Elecy | labour | SWR10524 | 185 | TO | 936.655
19 | 5.063 | Fabrication & erection of Channels Fabrication of Main and Auxiliary structures with power drilling using raw steel such as M.S.Angles, Plates, Channels, R.S.Joists, including the supply and fabrication of 6mm base and top plate for Box pole to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection. Fabrication of struc.with power drilling | Elecy | labour | SWR10868 | 6852 | TO | 34691.676
20 | 5.063 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. Sup Material for 1st coat Al. Painting. | Elecy | supply | SMR40009 | 2181 | TO | 11042.403
21 | 5.063 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium. Labour for 1st coat Al. Painting. | Elecy | labour | SWR10877 | 851 | TO | 4308.613
22 | 5.063 | Painting of sub-station structures with two coats of Aluminium paint usingAluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2ndcoat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. Sup Material for 2nd coat Al. Painting. | Elecy | supply | SMR40010 | 1293 | TO | 6546.459
23 | 5.063 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium . Labour for 2nd coat Al. Painting. | Elecy | labour | SWR10879 | 482 | TO | 2440.366
24 | 5.063 | Alligning the Main and Auxiliary structures such as RS joist, M.S.Angles, Plates, Channels, Structure to zero level duly leveling in prefabricated MS frames with Hydraulic jacks before galvanising/ fabrication | Elecy | labour | SWR10867 | 1470 | TO | 7442.61
25 | 13 | Loading of 33KV 800 Amps AB Switch | Elecy | labour | SWR10239 | 126 | EA | 1638
26 | 2 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading) Note: 1). It will be treated as full load of 10 MT and paid for 10 MT. 2). For 3 Ton vehicle : 50% of the following rates Transport of Cond Drum,VCBs >10 & <20Km | Elecy | labour | SWR11861 | 3299.7 | EA | 6599.4
27 | 13 | Un loading of 33KV 800 Amps AB Switch | Elecy | labour | SWR10557 | 79 | EA | 1027
28 | 13 | Erection of AB Switch and aligment complete Erection of 33 KV AB Switch including alignment and earthing | Elecy | labour | SWR10392 | 4500 | EA | 58500
29 | 38 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Note:-The requirement of 2nd coat is to be justified by the concerned Divisional Engineer /Executive Engineer before execution of this work Painting of operating rods of 33kV, 11kV AB switches with post office red colour (including cost of paint) | Elecy | labour | SWR10881 | 142 | EA | 5396
30 | 38 | Making of coil earthing pole with 8mm GI wireNut&Bolts for AB Switch AB Switch Coil Earthing GI No. 8 Wire | Elecy | labour | SWR12331 | 146.63 | EA | 5571.94
31 | 6 | Loading of 33 KV CTs/ PTs | Elecy | labour | SWR10200 | 165 | EA | 990
32 | 6 | Un loading of 33 KV CTs/ PTs | Elecy | labour | SWR10518 | 128 | EA | 768
33 | 2 | Erection of AB Switches, VCBs, LAs, PTs, CTs, DTRs etc Erection of 33kv single phase PT s | Elecy | labour | SWR10401 | 1079 | SET | 2158
34 | 12 | Loading of 33 KV, 10 KA LAs Station type | Elecy | labour | SWR10266 | 41 | EA | 492
35 | 12 | Un loading of 33 KV, 10 KA LAs Station type | Elecy | labour | SWR10584 | 35 | EA | 420
36 | 4 | Erection of AB Switches, VCBs, LAs, PTs, CTs, DTRs etc Erection of 33 KV LAS station/Line type including earthing | Elecy | labour | SWR10396 | 880 | SET | 3520
37 | 2 | Loading of 33 KV VCBs along with Panel boards | Elecy | labour | SWR10198 | 1024 | EA | 2048
38 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading) Note: 1). It will be treated as full load of 10 MT and paid for 10 MT. 2). For 3 Ton vehicle : 50% of the following rates Above 10 Km and upto 20 Km with Lorry for each trip Transport of Cond Drum,VCBs >10 & <20Km | Elecy | labour | SWR11861 | 3299.7 | EA | 3299.7
39 | 2 | Un loading of 33 KV VCBs along with Panel boards | Elecy | labour | SWR10516 | 1044.48 | EA | 2088.96
40 | 12.58 | Excavate-Pit for 33KV VCB | Elecy | labour | SWR23224 | 331 | M3 | 4163.98
41 | 14.52 | Cement concrete 1:3:6 ration with 40 MML HBG metal including the cost of all materials and labour complete 1.8 x 1.8 x 0.75 cum for VCB Plinth | Elecy | labour | SWR20685 | 5160 | M3 | 74923.2
42 | 2 | Erection of AB Switches, VCBs, LAs, PTs, CTs, DTRs etc Erection of 33 KV VCB with Control Panel | Elecy | labour | SWR10460 | 12500 | EA | 25000
43 | 2 | Loading and unloading of PTR on constructed plinth LOADING of 12.5 MVA PTR | Elecy | labour | SWR10614 | 12044.93 | EA | 24089.86
44 | 2 | Transport of Power transformers (0 to 100 KM) from one place to another place in GHMC Area.(excluding of loading & unloading ) Transport of 12.5MVA power transformer | Elecy | labour | SWR10855 | 27431 | EA | 54862
45 | 2 | UNLOADING of 12.5 MVA PTR | Elecy | labour | SWR10628 | 12044.93 | EA | 24089.86
46 | 700 | S/o rail poles 90/105lb (250x2N) | Elecy | supply | SMR22718 | 47.27 | KG | 33089
47 | 4 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation Erection of Rail Pole 90Lbs | Elecy | labour | SWR10344 | 3510 | EA | 14040
48 | 2 | Erection of PTR on constructed plinth Erection of 12.5 MVA PTR. | Elecy | labour | SWR10929 | 51818 | EA | 103636
49 | 0.44 | Extention of 33KV Bay at 132/33KV Sub-station 33KV Bay Extn: S-Zebra Conductor | Elecy | supply | SMR24910 | 299369 | KM | 131722.36
50 | 30 | Supply of Tension Hardware 3 Bolted for single Zebra/panther with 150 mm spacing. | Elecy | supply | SMR11915 | 2055 | SET | 61650
51 | 30 | Supply of clamps as per IS 5561- 1970 , 12mm thickness with Alluminum and Alluminum alloy conforming to A6 of IS 617 1994 & hot dip galvanised with Nuts & Bolts including spring washers conforming to IS 2633-1964, IS 1363-1967, IS1367-1961) Supply of I-Bolts | Elecy | supply | SMR22473 | 294 | EA | 8820
52 | 45 | Supply of clamps as per IS 5561- 1970 , 12mm thickness with Alluminum and Alluminum alloy conforming to A6 of IS 617 1994 & hot dip galvanised with Nuts & Bolts including spring washers conforming to IS 2633-1964, IS 1363-1967, IS1367-1961) Supply of Alluminum alloy T clamps conforming to A6 of IS 617, 4 bolted with hot dip galvanised bolts and double nuts with spring and flat washers of size M10 x 65 i.e(3/8" x 21/2 "to suit for panther ACSR on all three ways /on one side and Zebra ACSR on take off side or any other combination for carrying 800 A current rating . Sup T clamp LM6 Al alloy of 12 mm, 800 A | Elecy | supply | SMR40011 | 299 | EA | 13455
53 | 6 | Bus stringing Hoisting of Insulators and hardware, stretching the conductor and stringing of 33 kV bus comprising of three phases with Single Zebra/panther conductor to a tension of 450kgs.(Bussection of 4.5mt) Hoisting post ins&hrd wr 1panther 33kv | Elecy | labour | SWR21240 | 781 | EA | 4686
54 | 218.67 | Stringing of bus with panther conductor including jumpering etc., complete to all the equipment in SS fixing to all clamps and equipment.(3 Conductors) Stringing of bus with panther conductor | Elecy | labour | SWR10404 | 327.68 | M | 71653.7856
55 | 30 | Bus stringing Connection of equipment to bus and or another equipment with single zebra/Panther conductor including measuring, cutting,clamping and hoisting of suspension insulator assembly to support the conductor wherever necessary. | Elecy | labour | SWR10884 | 224 | EA | 6720
56 | 75 | Labour for Fixing of all types of clamps | Elecy | labour | SWR10917 | 65 | EA | 4875
57 | 29 | Loading of R.S. Joists 150 x 150mm / Rail poles | Elecy | labour | SWR10205 | 176 | EA | 5104
58 | 10.12 | Transport of iron materials such as R.S. Joists, Rail Poles, fabricated supports, steel, iron, flat, M.S. Channels etc., by lorries. (excluding of loading & unloading ) Above 10 KM and upto 20 KM | Elecy | labour | SWR10132 | 412.08 | TO | 4170.2496
59 | 29 | Un loading of R.S. Joists 150 x 150mm / Rail poles | Elecy | labour | SWR10523 | 107 | EA | 3103
60 | 29 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders) 9.1 Mtrs PSCC Poles 0.76 M x 0.76M x 1.83M (2.6" x 2.6" x 6.0") | Elecy | labour | SWR11039 | 928 | EA | 26912
61 | 10.12 | Fabrication of Main and Auxiliary structures with power drilling using raw steel such as M.S.Angles, Plates, Channels, R.S.Joists, including the supply and fabrication of 6mm base and top plate for Box pole to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection. Fabrication of struc.with power drilling | Elecy | labour | SWR10868 | 6852 | TO | 69342.24
62 | 10.12 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. Sup Material for 1st coat Al. Painting. | Elecy | supply | SMR40009 | 2181 | TO | 22071.72
63 | 10.12 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium Labour for 1st coat Al. Painting. | Elecy | labour | SWR10877 | 851 | TO | 8612.12
64 | 10.12 | Painting of sub-station structures with two coats of Aluminium paint usingAluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2ndcoat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. Sup Material for 2nd coat Al. Painting. | Elecy | supply | SMR40010 | 1293 | TO | 13085.16
65 | 10.12 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium . Labour for 2nd coat Al. Painting. | Elecy | labour | SWR10879 | 482 | TO | 4877.84
66 | 10.12 | Alligning the Main and Auxiliary structures such as RS joist, M.S.Angles, Plates, Channels, Structure to zero level duly leveling in prefabricated MS frames with Hydraulic jacks before galvanising/ fabrication | Elecy | labour | SWR10867 | 1470 | TO | 14876.4
67 | 29 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation Erection of RS Joist 150 x 150 mm | Elecy | labour | SWR10348 | 1952.61 | EA | 56625.69
68 | 32.19 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Mass concreting of supports incl. cement | Elecy | labour | SWR10356 | 6579 | M3 | 211778.01
69 | 16.75 | Plastering 2 coats, 20/16 mm (1:6)/(1:4) | Elecy | labour | SWR10862 | 373 | M2 | 6247.75
70 | 29 | Painting of poles Paint of coping with 2 coats of white cement incl cost of paints etc. Ptg of coping with 2cts white cmnt inclu | Elecy | labour | SWR11089 | 48 | EA | 1392
71 | 5.588 | Loading of M.S.Channels, Angles, Flats & Rods etc., | Elecy | labour | SWR10206 | 221 | TO | 1234.948
72 | 5.588 | Transport of iron materials such as R.S. Joists, Rail Poles, fabricated supports, steel, iron, flat, M.S. Channels etc., by lorries. (excluding of loading & unloading ) Above 10 KM and upto 20 KM | Elecy | labour | SWR10132 | 412.08 | TO | 2302.703
73 | 5.588 | Un loading of M.S.Channels, Angles, Flats & Rods etc., | Elecy | labour | SWR10524 | 185 | TO | 1033.78
74 | 5.588 | Fabrication of Main and Auxiliary structures with power drilling using raw steel such as M.S.Angles, Plates, Channels, R.S.Joists, including the supply and fabrication of 6mm base and top plate for Box pole to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection. Fabrication of struc.with power drilling | Elecy | labour | SWR10868 | 6852 | TO | 38288.976
75 | 5.588 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters ofthinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes,labour charges etc., complete. Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. Sup Material for 1st coat Al. Painting. | Elecy | Supply | SMR40009 | 2181 | TO | 12187.428
76 | 5.588 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium Labour for 1st coat Al. Painting. | Elecy | labour | SWR10877 | 851 | TO | 4755.388
77 | 5.588 | Painting of sub-station structures with two coats of Aluminium paint usingAluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2ndcoat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. Sup Material for 2nd coat Al. Painting. | Elecy | Supply | SMR40010 | 1293 | TO | 7225.284
78 | 5.588 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium . Labour for 2nd coat Al. Painting. | Elecy | labour | SWR10879 | 482 | TO | 2693.416
79 | 5.588 | Alligning the Main and Auxiliary structures such as RS joist, M.S.Angles, Plates, Channels, Structure to zero level duly leveling in prefabricated MS frames with Hydraulic jacks before galvanising/ fabrication | Elecy | labour | SWR10867 | 1470 | TO | 8214.36
80 | 2 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators,transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading) Note: 1). It will be treated as full load of 10 MT and paid for 10 MT. 2). For 3 Ton vehicle : 50% of the following rates Transport of Cond Drum,VCBs >10 & <20Km | Elecy | labour | SWR11861 | 3299.7 | EA | 6599.4
81 | 24 | Un loading of 11KV AB Switch Conventional type UNLOADING of 11 KV AB SWCH Con 200/400 A | Elecy | labour | SWR10556 | 80 | EA | 1920
82 | 21 | Erection of 11KV 800A double throw AB Switches | Elecy | labour | SWR21277 | 3500 | EA | 73500
83 | 3 | Erection of 11KV 400/200A Conventional type AB Switch including fixing of cross angles and alignment complete | Elecy | labour | SWR10393 | 3200 | EA | 9600
84 | 2 | Loading of 11 KV CT - PT Sets | Elecy | labour | SWR10201 | 190 | EA | 380
85 | 2 | Un loading of 11 KV CT - PT Sets | Elecy | labour | SWR10519 | 101 | EA | 202
86 | 2 | Erection of 11 KV three phase PTs | Elecy | labour | SWR10402 | 800 | SET | 1600
87 | 30 | Loading of 11 KV, 10 KA LAs Station type | Elecy | labour | SWR10264 | 32 | EA | 960
88 | 30 | Un Loading of 11 KV, 10 KA LAs Station type | Elecy | labour | SWR10582 | 32 | EA | 960
89 | 2 | Erection of 11 KV LAS station type including earthing | Elecy | labour | SWR10397 | 559 | SET | 1118
90 | 8 | Erection of 11 KV LAS line type including earthing | Elecy | labour | SWR10398 | 505 | SET | 4040
91 | 10 | Loading of 11 KV VCBs along with Panel boards | Elecy | labour | SWR10199 | 1024 | EA | 10240
92 | 5 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading) Note: 1). It will be treated as full load of 10 MT and paid for 10 MT. 2). For 3 Ton vehicle : 50% of the following rates Transport of Cond Drum,VCBs >10 & <20Km | Elecy | labour | SWR11861 | 3299.7 | EA | 16498.5
93 | 10 | Un Loading of 11 KV VCBs along with Panel boards | Elecy | labour | SWR10517 | 1044.48 | EA | 10444.8
94 | 52 | Excavate-Pit for 33KV VCB | Elecy | labour | SWR23224 | 331 | M3 | 17212
95 | 60 | Cement concrete 1:3:6 ration with 40 MML HBG metal including the cost of all materials and labour complete 1.8 x 1.8 x 0.75 cum for VCB Plinth | Elecy | labour | SWR20685 | 5160 | M3 | 309600
96 | 10 | Erection of 11 KV VCB with Control Panel | Elecy | labour | SWR10461 | 12000 | EA | 120000
97 | 12 | Supply of Tension Hardware 3 Bolted for single Zebra/panther with 150 mm spacing. | Elecy | Supply | SMR11915 | 2055 | SET | 24660
98 | 12 | Supply of clamps as per IS 5561- 1970 , 12mm thickness with Alluminum and Alluminum alloy conforming to A6 of IS 617 1994 & hot dip galvanised with Nuts & Bolts including spring washers conforming to IS 2633-1964, IS 1363-1967, IS1367- 1961) Supply of I-Bolts | Elecy | Supply | SMR22473 | 294 | EA | 3528
99 | 45 | Supply of clamps as per IS 5561- 1970 , 12mm thickness with Alluminum and Alluminum alloy conforming to A6 of IS 617 1994 & hot dip galvanised with Nuts & Bolts including spring washers conforming to IS 2633-1964, IS 1363-1967, IS1367- 1961) Supply of Alluminum alloy T clamps conforming to A6 of IS 617, 4 bolted with hot dip galvanised bolts and double nuts with spring and flat washers of size M10 x 65 i.e(3/8" x 21/2 " to suit for panther ACSR on all three ways /on one side and Zebra ACSR on take off side or any other combination for carrying 800 A current rating . Sup T clamp LM6 Al alloy of 12 mm, 800 A | Elecy | Supply | SMR40011 | 299 | EA | 13455
100 | 2 | Bus Stringing Hoisting of Insulators and hardware, stretching the conductor and stringing of 11 kV bus comprising of three phases with Single Zebra/panther conductor to a tension of 450kgs.(Bus section of 3.5mt) Hoisting post ins&hrd wr 1panther 11kv | Elecy | labour | SWR21241 | 507 | EA | 1014
101 | 45 | Connection of equipment to bus and or another equipment with single zebra/Panther conductor including measuring, cutting,clamping and hoisting of suspension insulator assembly to support the conductor wherever necessary. | Elecy | labour | SWR10884 | 224 | EA | 10080
102 | 57 | Labour for Fixing of all types of clamps | Elecy | labour | SWR10917 | 65 | EA | 3705
103 | 6.27 | Loading of M.S.Channels, Angles, Flats & Rods etc., | Elecy | labour | SWR10206 | 221 | TO | 1385.67
104 | 6.27 | Transport of iron materials such as R.S. Joists, Rail Poles, fabricated supports, steel, iron, flat, M.S. Channels etc., by lorries. (excluding of loading & unloading ) Above 10 KM and upto 20 KM | Elecy | labour | SWR10132 | 412.08 | TO | 2583.7416
105 | 6.27 | Un loading of M.S.Channels, Angles, Flats & Rods etc., | Elecy | labour | SWR10524 | 185 | TO | 1159.95
106 | 696 | Laying of earth mat including excavation of trenches of depth 600mm, welding, connecting to equipment and connecting lightning shield to earth mat and earthing of fence posts, drilling and connecting earth rods including connecting cast iron pipes with the following sizes of MS Flats /GI Flats. including fabrication 75x 8mm MS Flat / GI Flat. Laying of earth mat,excavation 75x 8mm | Elecy | labour | SWR10920 | 65 | RMT | 45240
107 | 1247 | Fabrication and connecting to risers from earth mat to structures, equipment, marshalling boxes, electrical panels, PLCC panels, fencing posts etc. M.S./ G.I. Flat 50x6mm / 50 x 8 mm ( Above ground) Earthing for raisers of SS Flat 50x6 mm. | Elecy | labour | SWR10919 | 41 | RMT | 51127
108 | 36 | Supply of CI earth pipe 100 mm dia, 2.75 mt long thickness 10mm with flange as per specication | Elecy | Supply | SMR11482 | 3486 | EA | 125496
109 | 36 | Providing of earthing with excavation of earth pit (0.6 x0.6x2.4 Mts.) duly filling with bentonite, earth , running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.75M dia x 0.5 M height | Elecy | labour | SWR10357 | 1234.2 | EA | 44431.2
110 | 36 | Providing of RCC collar to earth pit Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50 M height ERECT. OF LINES-Providing of RCC collar | Elecy | labour | SWR10359 | 386 | EA | 13896
111 | 2 | Supply of Copper Flexible jumper with 75 X 8 of length 250 mm at neutral of Power tranformer end and 50 X 6 of length 50mm two Nos at double neutral end duly brasing with flexible jumper of capacity of 5kA/3 sec for power transformer neutral. SupCU Flexi jumper for Power T/F Neutral | Elecy | Supply | SMR40033 | 4725 | EA | 9450
112 | 2 | Providing of double earthing for neutral with flexible copper jumpers including arrangement by fixing M.S.Channel 100x50mm. | Elecy | labour | SWR11892 | 1323 | EA | 2646
113 | 4 | Loading of LT AB Cable 3X16+25 Sqmm | Elecy | labour | SWR11702 | 200 | DR | 800
114 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading) Note: 1). It will be treated as full load of 10 MT and paid for 10 MT. 2). For 3 Ton vehicle : 50% of the following rates Transport of Cond Drum,VCBs>10 & <20Km | Elecy | labour | SWR11861 | 3299.7 | EA | 3299.7
115 | 4 | Un loading of LT AB Cable 3X16+25 Sqmm Drum | Elecy | labour | SWR11713 | 204 | DR | 816
116 | 90 | Providing of control cable trench as per DATA-XII | Elecy | labour | SWR22093 | 3148 | RMT | 283320
117 | 3312 | Control Cable Laying of 4 core/10 core 2.5 sq. mm.Copper control cable in aready excavation trench including cost of providing single compress glands at both ends . Lay-4C/10C 2.5Sqmm Control Cable | Elecy | labour | SWR11879 | 27 | M | 89424
118 | 270 | Cable terminations to the switch gear marshalling boxes/panel terminal blocks/control and relay panels LT AC panel including providing suitable ferrules and lugs as per specification (including cost of ferrules, lugs and glands) L-Cable Termination to Switchgear | Elecy | labour | SWR12510 | 27 | EA | 7290
119 | 4 | Supply of FRP PT Marshalling Box | Elecy | Supply | SMR40048 | 4463 | EA | 17852
120 | 4 | Erection of Marshalling boxes | Elecy | labour | SWR10940 | 374.85 | EA | 1499.4
121 | 1 | Loading of 220 V Batterry with charger | Elecy | labour | SWR11166 | 1612 | SET | 1612
122 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading) Note: 1). It will be treated as full load of 10 MT and paid for 10 MT. 2). For 3 Ton vehicle : 50% of the following rates Transport of Cond Drum,VCBs>10 & <20Km | Elecy | labour | SWR11861 | 3299.7 | EA | 3299.7
123 | 1 | Un loading of 220 V Batterry with charger | Elecy | labour | SWR11147 | 1024 | SET | 1024
124 | 1 | Erection of 220 V, 80 AH battery in complete shape fit for charging . Conventional lead acid | Elecy | labour | swr12295 | 7666 | EA | 7666
125 | 1 | Control Panels Supply of DC Annunciation & relay panel for 10 feeder panel including the cost of LED Indiacation lamps, VAA auxilairy relays, Electronic Hooters complete as per specification. Supply of DC Anunc.relay panel 8 feeders | Elecy | Supply | SMR40044 | 42500 | EA | 42500
126 | 1 | Supply of AC Supply panel inluding providing of changeover switch, SFU, metering unit, 32 A three phase MCB, 16 A Single phase MCB complete as per specification. Supply of AC Supply panel complete | Elecy | Supply | SMR40045 | 42000 | EA | 42000
127 | 8 | Supply of stepped tubular poles single way made of steel of length 9mtrs with tensile strength of 42kgf/mm2 at a steps of 4.5 mtrs with outer dia 114.3 mm,2.1 mtrs with outer dia 88.9 mm, 2.1 mtrs with outer dia 76.1 mm, normal Crippling load of 141 kgf, normal Breaking load of 198 kgf ,working Crippling load of 70 kgf, working Breaking load of 79 kgf as per IS 2713. Supply 9mtrs tubular poles single way | Elecy | Supply | SMR40051 | 13913 | EA | 111304
128 | 8 | Supply of LED fixture set of (LUMINAIRE MAKE: PHILIPS /OSRAM/GE/VENTURE/CROMPTON/BAJAJ/VIN/WIPRO/JAGUAR/KESELEC/HAVELLS/HPL/SURYA/SYSKA. LED MAKE: PHILIPS LUMILEDS/CREE/NICHIA /OSRAM /SUMSANG/LG LEDs) make with minimum 120 Lm/W Lumens Output, 105 V to 295 V Voltage range, more than 0.94 Power factor, Pressure Die cast Alluminium housing, Powder coated/ anodized finishing, toughed glass lamp cover, IP65 ingress protection, less than 25% THD, minimum 70% electronic efficiency, minimum 140 degrees along the road & 80 degrees across the road beam angle, 4500 to 6500K Color temperature, very low mercury 6.4mg max, Life more than 50,000 burning hours, maximum 20% depreciation during life, Fully cut off control of distribution, Electronic Ballast driver type, minimum 10KV Surge withstand capacity, Poly carbonate reflector/ Poly Carbonate Lens secondary optics, suitable for fixing to existing poles in the Substations, with five years warranty S-90W LED fixture set | Elecy | Supply | SMR11594 | 8200 | EA | 65600
129 | 8 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders) 9.1 Mtrs PSCC Poles 0.76 M x 0.76M x 1.83M (2.6" x 2.6" x 6.0") Exca Hard pit w/o blast 0.76X0.76X1.83M | Elecy | labour | SWR11039 | 928 | EA | 7424
130 | 8 | Erection of tubular poles | Elecy | labour | SWR10955 | 1379 | EA | 11032
131 | 5.27 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Mass concreting of supports incl. cement | Elecy | labour | SWR10356 | 6579 | M3 | 34671.33
132 | 8 | Fixing of LED/Metal halide complete. | Elecy | labour | SWR10956 | 1268 | EA | 10144
133 | 45 | Supply & spreading of 20mm machine crushed metal (HBG) including cost of conveneyance of all materials, labour charges etc complete for finished item of work and directed by the engineer incharge Supply & Spreading of 20mm HBG metal | Elecy | labour | SWR10860 | 2113 | M3 | 95085
134 | 3 | LOADING of R.S. Joists 175 x 85 mm | Elecy | labour | SWR10204 | 76 | EA | 228
135 | 0.75 | Transport of iron materials such as R.S. Joists, Rail Poles, fabricated supports, steel, iron, flat, M.S. Channels etc., by lorries. (excluding of loading & unloading ) TRANSPORT OF STEEL 10 TO 20KM | Elecy | labour | SWR10132 | 412.08 | TO | 309.06
136 | 3 | UNLOADING of R.S. Joists 175x 85 mm | Elecy | labour | SWR10522 | 50 | EA | 150
137 | 2 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders) 11 Mtrs PSCC Poles/ Box poles 0.75 M x 0.9 M x 1.95 M Ex of Hard pit w/o blast 0.75X0.9X1.95M | Elecy | labour | SWR11040 | 990.68 | EA | 1981.36
138 | 0.75 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete . Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. Sup Material for 1st coat Al. Painting. | Elecy | Supply | SMR40009 | 2181 | TO | 1635.75
139 | 0.75 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium Labour for 1st coat Al. Painting. | Elecy | labour | SWR10877 | 851 | TO | 638.25
140 | 0.75 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. (*)Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. Sup Material for 2nd coat Al. Painting. | Elecy | Supply | SMR40010 | 1293 | TO | 969.75
141 | 0.75 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. (*) Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium Labour for 2nd coat Al. Painting. | Elecy | labour | SWR10879 | 482 | TO | 361.5
142 | 1 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation Erect-12Meter Box pole | Elecy | labour | SWR11267 | 3901.37 | EA | 3901.37
143 | 2.22 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc Mass concreting of supports incl. cement | Elecy | labour | SWR10356 | 6579 | M3 | 14605.38
144 | 1.16 | Plastering 2 coats, 20/16 mm (1:6)/(1:4) | Elecy | labour | SWR10862 | 373 | M2 | 432.68
145 | 2 | Painting of poles Paint of coping with 2 coats of white cement incl cost of paints etc. Ptg of coping with 2cts white cmnt inclu | Elecy | labour | SWR11089 | 48 | EA | 96
146 | 1 | Construction of DTR Plinth RCC Column type DTR Plinth of size 1'X1'X10',topslab 4'x4'x6" & beam size 4'X8'X8" upto 160KVA Column type DTR Plinth topslab 4'x4'x6" | Elecy | labour | SWR21843 | 25967.57 | EA | 25967.57
147 | 1 | LOADING of 50,63,75&100kva DTR | Elecy | labour | SWR10195 | 350 | EA | 350
148 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading) Note: 1). It will be treated as full load of 10 MT and paid for 10 MT. 2). For 3 Ton vehicle : 50% of the following rates Transport of Cond Drum,VCBs>10 & <20Km | Elecy | labour | SWR11861 | 3299.7 | EA | 3299.7
149 | 1 | UNLOADING of 50,63,75&100kva DTR | Elecy | labour | SWR10513 | 280 | EA | 280
150 | 1 | Erection of DTR's including loading and Unloading DTR on the Structure/Plinth etc Erection of 3 Phase DTRs 63,75 & 100 KVA E/r 3ph DTR inclu L&Un-L,T&C on plinth | Elecy | labour | SWR20905 | 1650 | EA | 1650
151 | 1 | LOADING of 11 KV AB SWCH T.T.200/400 A | Elecy | labour | SWR12406 | 80 | EA | 80
152 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading) Note: 1). It will be treated as full load of 10 MT and paid for 10 MT. 2). For 3 Ton vehicle : 50% of the following rates Transport of Cond Drum,VCBs>10 & <20Km | Elecy | labour | SWR11861 | 3299.7 | EA | 3299.7
153 | 1 | Un loading of 11 KV AB SWCH T.T.200/400 A | Elecy | labour | SWR12425 | 80 | EA | 80
154 | 1 | Erection of AB Switch and aligment complete Erection of 11KV 200A TT type AB Switch including fixing of cross angles and alignment complete | Elecy | labour | SWR20102 | 1813.49 | EA | 1813.49
155 | 1 | LOADING of 11 KV HG Fuse Sets | Elecy | labour | SWR10231 | 18 | EA | 18
156 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading) Note: 1). It will be treated as full load of 10 MT and paid for 10 MT. 2). For 3 Ton vehicle : 50% of the following rates Transport of Cond Drum,VCBs>10 & <20Km | Elecy | labour | SWR11861 | 3299.7 | EA | 3299.7
157 | 1 | UNLOADING of 11 KV HG Fuse Sets | Elecy | labour | SWR10549 | 18 | EA | 18
158 | 1 | Erection of AB Switches, VCBs, LAs, PTs, CTs, DTRs etc Erect. of 11kv HG Fuseset incl earthing | Elecy | labour | SWR10395 | 740.52 | SET | 740.52
159 | 40 | Excavation & laying of UG Cable in Single Run Laying of XLPE UG cable including excavation of trench of size 450mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV form road level, providing of DWC/GI pipes whereever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc.depth of the trench) LT -0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs. In Hard Gravel Soil / BC soil / Red earth / stone and earth mixed with fair boulders /Normal soil / CC/BT Road Lay-SR 11KV 3x185sqmm UG Cb HG/BC/CC/BT | Elecy | labour | SWR11920 | 465.46 | M | 18618.4
160 | 20 | Raising of cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe) Raise-SR 11KV 3x185sqmm UG Cb on support | Elecy | labour | SWR11956 | 126.23 | M | 2524.6
161 | 2 | UG Cables Joints Making of Outdoor/Indoor End Termination OD/Idoor end termination 11kv 3x185 xlpe | Elecy | labour | SWR10390 | 2370.63 | EA | 4741.26
162 | 1 | Erection of LT distribution box including laying of LT cable from distribution box to LT OH line and DTR to distribution box including earthing of distribution box and crimping of lugs connecting of jumpers etc Erection of LT distribution box | Elecy | labour | SWR10674 | 1594.67 | EA | 1594.67
163 | 85 | Excavation & laying of UG Cable in Single Run Laying of XLPE UG cable including excavation of trench of size 450mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV form road level, providing of DWC/GI pipes whereever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc.depth of the trench) LT -0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs.In Hard Gravel Soil / BC soil / Red earth / stone and earth mixed with fair boulders / Normal soil / CC/BT Road Lay-SR LT 3.5x95sqmm UG Cb HG/BC/CC/BT | Elecy | labour | swr11925 | 377.63 | M | 32098.55
164 | 15 | Raising of cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe) Raise-SR LT 3.5x95sqmm UG CB ON SUPPORT | Elecy | labour | SWR11961 | 85.43 | M | 1281.45
165 | 2 | UG Cables Joints Making of Outdoor/Indoor End Termination Sup of 31/2x185Sqmm UG O/D end term kits | Elecy | supply | SMR40140 | 550 | EA | 1100
166 | 2 | UG Cables Joints Making of Outdoor/Indoor End Termination Fixing of Out Door/Indoor end termination LT 3 1/2 x185 Sqmm Cable OD/Idoor end termination LT 3 1/2 x 185 | Elecy | labour | SWR10765 | 968.9 | EA | 1937.8
167 | 1 | Supply and fixing of Substation board of size 3'x2.5' indicating the layout of switchyard Sup &fix of board ind Switchyard layout | Elecy | labour | SWR20032 | 1654 | EA | 1654
168 | 1 | Supply and fixing of safety instructions/Substation operation instruction board. Sup& fix safety inst/SS Op. inst board | Elecy | labour | SWR22090 | 2205 | EA | 2205
169 | 750 | Control Panels Supplying & fabrication erection of 6mm Checkerd plates as per the field conditions Supply,fabricati of 6mm Checkerd plates | Elecy | labour | SWR10873 | 83 | KG | 62250
170 | 1 | T & P Supply of Wall clock standard make | Elecy | Supply | SMR40059 | 578 | EA | 578
171 | 1 | S-10ft Aluminium Ladder | Elecy | supply | SMR12378 | 1654 | EA | 1654
172 | 1 | Sup Alluminium Ladder for indoor works | Elecy | Supply | SMR40062 | 4410 | EA | 4410
173 | 30 | T & P Painting of Name Plates for any equipmen | Elecy | labour | SWR10963 | 122 | EA | 3660
174 | 1 | T & P Supply of Taparia Tool kit of Size 20”x10”x15” with tier arrangements Tool box with locking arrangement & key containing (1) Double Ended fix Spanner sets, (Ribbed) 6 x 7, 8 x 9, 10 x 11, 12 x 13, 14 x 15, 16 x 17, 18 x19, 20 x 22, 21 x 23, 24 x 27, 25 x28, 30 x 32, (2) Double Ended Ring Spanners sets, 6 x 7 , 8 x 9, 10 x 11, 12 x 13, 14 x 15. 16 x 17 , 18 x 19, 20 x 22 , 21 x 23, 24 x 27, 25 x28, 30 x 32 mm, (3) Adjustable Spanner 305 mm length least maximum opening 35mm chrome, (4) Pipe Wrench Length 350 mm 14”, (5) Soft faced Hammer with suitable handle 2 lb, (6) Hacksaw frame with metal handle heavy duty for 12" hacksaw blade with High Speed blade, (7) Insulated Screw drivers Transparent Green Handle Set Length 6”, 8” & 12”, (8) Star Screw Driver Transparent Green Handle Length 6”, (9) Insulated Wire Cutter, (10) Insulated Cutting Plier Length 8” with cable stripper insulated with thick C. A. sleeve confirming to IS: 4378 - 1990, (11) Long Nose Plier insulated with thick C.A. sleeve generally confirming to IS:3552-1989, (12) Tester type screw driver (special with neon bulb) generally confirm to IS: 5579- 1985 Grade:II handle yellow/ green colour overall length 130 mm, (13) Insulated Crimping Plier of all Taparia make. SupTaparia Tool kit complete as per Spec | Elecy | supply | SMR40063 | 4925 | SET | 4925
175 | 1 | T & P Sup Rechargeable LED torch light of Standard make | Elecy | supply | SMR40064 | 1733 | EA | 1733
176 | 1 | T & P Sup Steel almarah(61/2 X 3ft) Godrej | Elecy | supply | SMR40061 | 9818 | EA | 9818
177 | 1 | T & P Supply of Table (3x6ft) Godrej | Elecy | supply | SMR40057 | 6050 | EA | 6050
178 | 4 | T & P Supply of S type chairs (Godrej) | Elecy | supply | SMR40058 | 924 | EA | 3696
179 | 1 | T & P Sup Angle racks(18x36.6inches) Godrej | Elecy | supply | SMR40060 | 1733 | EA | 1733
180 | 1 | T & P Supply of Hack saw (12 inches) | Elecy | supply | SMR40065 | 289 | EA | 289
181 | 4 | Sup Earth Rods (8ft) Screw & clamp type | Elecy | supply | SMR40066 | 578 | EA | 2312
182 | 2 | Supply of Hand Gloves | Elecy | supply | SMR40067 | 289 | SET | 578
183 | 12 | SupRubber mats( 6'x3')size fo indoorSS | Elecy | supply | SMR40068 | 1386 | EA | 16632
184 | 1 | Biometric Time attendence System & Telecom Sup Stand basic cell phone with charger | Elecy | supply | SMR40069 | 1386 | EA | 1386
185 | 14 | Supply of Danger boards with clamps | Elecy | supply | SMR40070 | 116 | EA | 1624
186 | 2 | Supply of Materials Fire bucket stand with 3 buckets (8 -10 ltr capacity) Sup Fire Buckets Stand with Buckets | Elecy | supply | SMR40088 | 1386 | SET | 2772
187 | 2 | Room fire extinguisher (2 ltrs capacity) for control room Sup Fire Extinguisher for Control Room | Elecy | supply | SMR40089 | 4620 | EA | 9240
188 | 4 | Sup TrollyMounted Co2 (6.5Kgs) Cylinders(IS-2878) | Elecy | supply | SMR40087 | 9240 | EA | 36960
189 | 6 | Supply of Safety Helmet of standard make | Elecy | supply | SMR40071 | 231 | EA | 1386
190 | 8 | Supply of LC Boards | Elecy | supply | SMR40072 | 116 | EA | 928
191 | 4 | Supply of Gum Boots (pair) | Elecy | supply | SMR40073 | 693 | EA | 2772
192 | 1 | Supply of 5000v megger | Elecy | supply | SMR40074 | 13860 | EA | 13860
193 | 1 | Supply of Earth megger (1000v) | Elecy | supply | SMR40075 | 8085 | EA | 8085
194 | 1 | Supply of Digital clamp meter. | Elecy | supply | SMR40076 | 2888 | EA | 2888
195 | 1 | Name board of the 33/11kV Sub-Station(As per Standard Specification) Sup 33/11kv S.S Permanent name board | Elecy | supply | SMR40086 | 10238 | EA | 10238
196 | 800 | Supply of Hot dip galvanized/zinc coated bolts & nuts including spring washers, pack washers and flat washers etc. S-Hot dip gal./Zinc bolts & nuts washer | Elecy | supply | SMR12488 | 90 | KG | 72000
197 | 4 | LOADING of R.S. Joists 175 x 85 mm | Elecy | labour | SWR10204 | 76 | EA | 304
198 | 1 | Transport of iron materials such as R.S. Joists, Rail Poles, fabricated supports, steel, iron, flat, M.S. Channels etc., by lorries. (excluding of loading & unloading ) TRANSPORT OF STEEL 10 TO 20KM | Elecy | labour | SWR10132 | 412.08 | TO | 412.08
199 | 4 | UNLOADING of R.S. Joists 175x 85 mm | Elecy | labour | SWR10522 | 50 | EA | 200
200 | 4 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rockboulders) 8.0Mtrs PSCC Poles 0.76 M x 0.76M x 1.52M (2.6" x 2.6" x 5.0') 0.88 cum Ex of Hard pit w/o blast 0.76X0.76X1.52M | Elecy | labour | SWR11037 | 793 | EA | 3172
201 | 1 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. Sup Material for 1st coat Al. Painting. | Elecy | supply | SMR40009 | 2181 | TO | 2181
202 | 1 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., completeLabour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium Labour for 1st coat Al. Painting. | Elecy | labour | SWR10877 | 851 | TO | 851
203 | 1 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete (*)Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. Sup Material for 2nd coat Al. Painting. | Elecy | supply | SMR40010 | 1293 | TO | 1293
204 | 1 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete (*) Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium . Labour for 2nd coat Al. Painting. | Elecy | labour | SWR10879 | 482 | TO | 482
205 | 3.51 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Mass concreting of supports incl. cement | Elecy | labour | SWR10356 | 6579 | M3 | 23092.29
206 | 2.31 | Plastering 2 coats, 20/16 mm (1:6)/(1:4) | Elecy | labour | SWR10862 | 373 | M2 | 861.63
207 | 4 | Painting of poles Paint of coping with 2 coats of white cement incl cost of paints etc. Ptg of coping with 2cts white cmnt inclu | Elecy | labour | SWR11089 | 48 | EA | 192
208 | 5 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation Erection of RS Joists 150x75/175 x 85 mm | Elecy | labour | SWR10346 | 1934 | EA | 9670
209 | 24 | LOADING of 11 KV AB SWCH Con 200/400 A | Elecy | labour | SWR10238 | 80 | EA | 1920
210 | 2 | Fixing of AC/DC Panel and giving Connections to the protection equipment and Metering circuits as per the specification and standards. The 3 1/2 core 25 Sqmm power cable required from distribution box to AC/DC panel in the control room is also to be supply | Elecy | labour | SWR20025 | 7871.85 | SET | 15743.7
211 | 2 | Fabrication of 175x85/150x75mm RS joist pieces upto 12.5 meters length by welding joint together by means of 50x6mm flat and MS channel on either side including the cost of consumable. | Elecy | labour | SWR10642 | 512.55 | EA | 1025.1
sub total | [7 empty] | 3865350.0587
Bay extension
212 | 6.29 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders) (other than SS) Earth work excav hard rock bould <3cum | Elecy | labour | SWR10856 | 1318.35 | M3 | 8292.4215
213 | 7.26 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Mass concreting of supports incl. cement | Elecy | labour | SWR10356 | 6579 | M3 | 47763.54
214 | 1.8 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. Sup Material for 1st coat Al. Painting. | Elecy | supply | SMR40009 | 2181 | TO | 3925.8
215 | 1.8 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. (*)Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. Sup Material for 2nd coat Al. Painting. | Elecy | supply | SMR40010 | 1293 | TO | 2327.4
216 | 1.8 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., 1complete. Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium Labour for 1st coat Al. Painting. | Elecy | labour | SWR10877 | 851 | TO | 1531.8
217 | 1.8 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. (*) Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium Labour for 2nd coat Al. Painting. | Elecy | labour | SWR10879 | 482 | TO | 867.6
218 | 2 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation Erection of RS Joist 150 x 150 mm | Elecy | labour | SWR10348 | 1952.61 | EA | 3905.22
219 | 895 | Laying of 4 core/10 core 2.5 sq. mm.Copper control cable in aready excavation trench including cost of providing single compress glands at both ends . Lay-4C/10C 2.5Sqmm Control Cable | Elecy | labour | SWR11879 | 27 | M | 24165
220 | 2 | Sup MS Powder coated CT Marshalling Box | Elecy | supply | SMR40047 | 3675 | EA | 7350
221 | 2 | Erection of Marshalling boxes | Elecy | labour | SWR10940 | 374.85 | EA | 749.7
222 | 12 | Supply of Tension Hardware 3 Bolted for single Zebra/panther with 150 mm spacing. S-Tension HW 3Bolt 1Zebra/Pnthr 150mm | Elecy | supply | SMR11915 | 2055 | SET | 24660
223 | 32 | Laying of earth mat including excavation of trenches of depth 600mm, welding, connecting to equipment and connecting lightning shield to earth mat and earthing of fence posts, drilling and connecting earth rods including connecting cast iron pipes with the following sizes of MS Flats /GI Flats. including fabrication 75x 8mm MS Flat / GI Flat. Laying of earth mat,excavation 75x 8mm | Elecy | labour | SWR10920 | 65 | RMT | 2080
224 | 5 | Supply of earthing pipe with materials Supply of CI earth pipe 100 mm dia, 2.75 mt long thickness 10mm with flange as per specication S-CI Pipe earthing 100mm dia 2.75m long | Elecy | supply | SMR11482 | 3486 | EA | 17430
225 | 5 | Providing of earthing with excavation of earth pit (0.6 x0.6x2.4Mts.) duly filling with bentonite, earth , running of earth wireetc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.75M dia x 0.5 M height ERECT. OF LINES-Providing of earthing | Elecy | labour | SWR10357 | 1234.2 | EA | 6171
226 | 5 | Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X0.50 M height ERECT. OF LINES-Providing of RCC collar | Elecy | labour | SWR10359 | 386 | EA | 1930
227 | 6 | Bus Stringing Hoisting of Insulators and hardware, stretching the conductorand stringing of 33 kV bus comprising of three phases withSingle Zebra/panther conductor to a tension of 450kgs.(Bussection of 4.5mt) Hoisting post ins&hrd wr 1panther 33kv | Elecy | labour | SWR21240 | 781 | EA | 4686
228 | 200 | Cable terminations to the switch gear marshalling boxes/panelterminal blocks/control and relay panels LT AC panel including providing suitable ferrules and lugs as per specification (including cost of ferrules, lugs and glands) Lay-Cable Terminations to Switchgear | Elecy | labour | SWR11880 | 34.43 | EA | 6886
229 | 1 | Erection of AB Switches, VCBs, LAs, PTs, CTs, DTRs etc Erection of 33 KV LAS station/Line type including earthing Erect of 33kv LA stn type incl earthing | Elecy | labour | SWR10396 | 880 | SET | 880
230 | 1 | Erection of AB Switches, VCBs, LAs, PTs, CTs, DTRs etc Erection of 33kv VCB with Control Panel | Elecy | labour | SWR10460 | 12500 | EA | 12500
231 | 7.5 | Supply of HBG metal Supply & spreading of 20mm machine crushed metal (HBG)including cost of conveneyance of all materials, labour charges etc complete for finished item of work and directed by the engineer incharge Supply & Spreading of 20mm HBG metal | Elecy | labour | SWR10860 | 2113 | M3 | 15847.5
232 | 2 | Painting of sub-station structures with two coats of Aluminium paint usingAluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2ndcoat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Painting of operating rods of 33kV, 11kV AB switches withpost office red colour (including cost of paint) Painting AB switch OP rods with PO red | Elecy | labour | SWR10881 | 142 | EA | 284
233 | 1 | LOADING of 33 KV VCBs&Panel boards | Elecy | labour | SWR10198 | 1024 | EA | 1024
234 | 1 | UNLOADING of 33 KV VCBs&Panel boards | Elecy | labour | SWR10516 | 1044.48 | EA | 1044.48
235 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs,control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excludingof loading unloading) Transport of Cond Drum,VCBs upto 10Km | Elecy | labour | SWR11860 | 2720.34 | EA | 2720.34
236 | 2 | Erection of 33kv ABSwitch including alignment and earthing | Elecy | labour | SWR10392 | 4500 | EA | 9000
237 | 2 | Excavation of pits in all soils except hard rock requiring blasting 12Mtrs/Spun Pole 0.92 M x 0.92M x 2.3M (3.0" x 3.0" x 7.6") 1.94 cum EXCAVATION OF PIT(3.0" x 3.0" x 7.6") | Elecy | labour | SWR10109 | 842.78 | EA | 1685.56
238 | 48 | Labour for Fixing of all types of clamps | Elecy | labour | SWR10917 | 65 | EA | 3120
239 | 20 | Stringing of bus with panther conductor including jumpering etc., complete to all the equipment in SS fixing to all clampsand equipment.(3 Conductors) Stringing of bus with panther conductor | Elecy | labour | SWR10404 | 327.68 | M | 6553.6
240 | 45 | Fabrication of materials including 2 coats of Red oxide painting Fab Back clamps with 50 x 6 mm MS Flat | Elecy | labour | SWR10320 | 15 | EA | 675
241 | 2.114 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metalincluding the cost of metal, sand, Cement and curing etc. Mass concreting of supports incl. cement | Elecy | labour | SWR10356 | 6579 | M3 | 13908.006
242 | 2 | LOADING of RSJoists150 x 150 mm/RailPole | Elecy | labour | SWR10205 | 176 | EA | 352
243 | 1 | Transport of iron materials such as R.S. Joists, Rail Poles, fabricated supports, steel,iron, flat, M.S. Channels etc., by lorries. (excluding of loading & unloading ) TRANSPORT OF STEEL 10 TO 20KM | Elecy | labour | SWR10132 | 412.08 | TO | 412.08
244 | 2 | UNLOADING of RSJoists150 x150 mm/RailPol | Elecy | labour | SWR10523 | 107 | EA | 214
245 | 1.8 | Fabrication of Main and Auxiliary structures with welding usingraw steel such as RS joist, M.S.Angles, Plates, Channels,including the supply and fabrication of 6mm base plate to theRS-Joist poles excluding cost of Mild Steel and transportcharges to substation site, including erection. Fabrication of struc.with welding. | Elecy | labour | SWR10869 | 3426 | TO | 6166.8
sub total | [7 empty] | 241108.8475
33Kv LINE LABOUR
246 | 8 | survey line&cabl inc peg mark&tree clear | Elecy | labour | SWR22092 | 765 | KM | 6120
247 | 50 | S-M+3 Tower GALV | Elecy | supply | SMR11683 | 140674.3 | EA | 7033715
248 | 50 | Supply of material for Extension of 3Mtrs for M+3 (Galvanized) S-Mat. for Extn of M+3 Tower by 3M GALV | Elecy | supply | SMR11684 | 28520.64 | EA | 1426032
249 | 50 | Erect- M+3 Tower GALV | Elecy | labour | SWR11850 | 64576 | EA | 3228800
250 | 50 | Erect-Extn of 3M for M+3 Tower GALV | Elecy | labour | SWR11851 | 5168.95 | EA | 258447.5
251 | 237.6 | Earth work excavation of pits in hard murram/rock boulders Excavate-Earth in Hard Murram | Elecy | labour | SWR20959 | 1530 | M3 | 363528
252 | 4 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders) 12Mtrs/Spun Pole 0.92 M x 0.92M x 2.3M (3.0" x 3.0" x 7.6") Exc of Hard pit w/o blast 0.92X0.92X2.3M | Elecy | labour | SWR11041 | 1466.25 | EA | 5865
253 | 4 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation. Erect-12Meter Box pole | Elecy | labour | SWR11267 | 3901.37 | EA | 15605.48
254 | 8 | Fabrication of 175x85/150x75mm RS joist pieces upto 12.5 meters length by welding joint together by means of 50x6mm flat and MS channel on either side including the cost of consumable. Fabrication of 175x85/150x75mm RS joist | Elecy | labour | SWR10642 | 512.55 | EA | 4100.4
255 | 8 | Painting of poles Painting of R.S Joist,Box poles including cross arms and clamps with one coat of red oxid and two coats of Al.paint including cost of paint and consumables Painting of RS Joist(1C RO, 2C Al.Paint) | Elecy | labour | SWR10640 | 1132 | EA | 9056
256 | 4.41 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Including the cost of cement | Elecy | labour | SWR10356 | 6579 | M3 | 29013.39
257 | 20 | Formation of Cut point for 33 KV Double circuit line excluding pole erection and stays Formation of 33kvline vertical cutpoint | Elecy | labour | SWR10466 | 3198.72 | EA | 63974.4
258 | 6.4 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. Sup Material for 1st coat Al. Painting. | Elecy | supply | SMR40009 | 2181 | TO | 13958.4
259 | 6.4 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium Labour for 1st coat Al. Painting. | Elecy | labour | SWR10877 | 851 | TO | 5446.4
260 | 6.4 | Painting of sub-station structures with two coats of Aluminium paint usingAluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2ndcoat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. Sup Material for 2nd coat Al. Painting. | Elecy | supply | SMR40010 | 1293 | TO | 8275.2
261 | 6.4 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium . Labour for 2nd coat Al. Painting. | Elecy | labour | SWR10879 | 482 | TO | 3084.8
262 | 8 | Paving out and stringing of conductor by providing temporary stays, tensioning, sagging correctly, fixing strain points, transferring to pin points binding, keeping stifner, rectification of poles, guys and jumpering etc., including transport of material from road side to location. 100 Sqmm Single Circuit (3 Conductors) Stringing 100sqmm 33/11kv Line 3 Cond SC | Elecy | labour | SWR10366 | 13856.7 | KM | 110853.6
263 | 8.4 | Transport of steel including line materials such as cross arms, clamps, hardware,cable (loose) and other line materials (Including loading and unloading) TRANSPORT OF STEEL MATERIAL 20 TO 30KM | Elecy | labour | SWR10149 | 527.34 | TO | 4429.656
264 | 6.4 | LOADING of MS Channel,Angles,Flats&Rods | Elecy | labour | SWR10206 | 221 | TO | 1414.4
265 | 6.4 | UNLOADING of MS Channel,Angles,Flats&Rod | Elecy | labour | SWR10524 | 185 | TO | 1184
266 | 480 | LOADING of 33 KV Pin insulators | Elecy | labour | SWR10211 | 3 | CRT | 1440
267 | 480 | UNLOADING of 33 KV Pin insulators | Elecy | labour | SWR10529 | 3 | CRT | 1440
268 | 8 | LOADING of 33KV Metal parts-bag of 25no | Elecy | labour | SWR10618 | 65 | BAG | 520
269 | 4 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading) Note: 1). It will be treated as full load of 10 MT and paid for 10 MT. 2). For 3 Ton vehicle : 50% of the following rates Above 20 Km and upto 30 Km with Lorry for each trip Transport of Cond Drum,VCBs>20 & <30Km | Elecy | labour | SWR11862 | 3691.38 | EA | 14765.52
270 | 50 | S-GI Bolts & Nuts,Washers etc., | Elecy | supply | SMR11488 | 117.5 | KG | 5875
271 | 6 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading) Note: 1). It will be treated as full load of 10 MT and paid for 10 MT. 2). For 3 Ton vehicle : 50% of the following rates Above 20 Km and upto 30 Km with Lorry for each trip Transport of Cond Drum,VCBs>20 & <30Km | Elecy | labour | SWR11862 | 3691.38 | EA | 22148.28
272 | 12 | Load-11/33KV XLPE UG Cable for all sizes | Elecy | labour | SWR11230 | 1024 | DR | 12288
273 | 12 | Unload-11/33KV XLPE UG Cable all sizes | Elecy | labour | SWR11231 | 1024 | DR | 12288
274 | 1700 | Excavation & laying of UG Cable (Double Run) Laying of XLPE UG cable Double Run including excavation of trench of size 600mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV from road level and cable separation with machine cut bricks horizontally for every 3 meters , providing of DWC/GI pipes wherever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and removing the debris from the site inluding the cost of lead and lift etc.. (Second cable laying cost not Included) depth of the trench LT-0.85 mts, Along the CC / BT multi layer road requiring compressor 33 KV 3x400 Sqmm Cable Lay-DR 33KV 3x400sqmm UG Cb CC/BT Compsr | Elecy | labour | SWR11980 | 1388.84 | M | 2361028
275 | 1700 | Lay-2nd Cable in Excavated Trench | Elecy | labour | SWR10988 | 204.1 | M | 346970
276 | 200 | Excavation & laying of UG Cable in Single Run Laying of XLPE UG cable including excavation of trench of size 450mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV form road level, providing of DWC/GI pipes whereever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc.depth of the trench) LT -0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs. Raising of cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe) Raise-SR 33KV 3x400sqmm UG Cb on support | Elecy | labour | SWR11954 | 135.66 | M | 27132
277 | 12 | Making of Outdoor/Indoor End Making 33 KV 3x400 Sqmm Cable Out Door/Indoor end termination TerminationOD/Idoor end termination 33kv 3x400 xlpe | Elecy | labour | SWR10387 | 2764.76 | EA | 33177.12
278 | 8 | UG Cables Joints 33 KV 3x400 Sqmm Cable Straight through joint 33kv 3x400 xlpe | Elecy | labour | SWR10382 | 5700.78 | EA | 45606.24
279 | 2 | Erection of AB Switch and aligment complete Erection of 33 KV AB Switch including alignment and earthing | Elecy | labour | SWR10392 | 4500 | EA | 9000
280 | 2 | Painting of sub-station structures with two coats of Aluminium paint usingAluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2ndcoat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Painting of operating rods of 33kV, 11kV AB switches withpost office red colour (including cost of paint) Painting AB switch OP rods with PO red | Elecy | labour | SWR10881 | 142 | EA | 284
281 | 8 | LOADING of R.S. Joists 175 x 85 mm | Elecy | labour | SWR10204 | 76 | EA | 608
282 | 8 | UNLOADING of R.S. Joists 175 x 85 mm | Elecy | labour | SWR10522 | 50 | EA | 400
283 | 8 | LOADING of Conductor drums | Elecy | labour | SWR10191 | 202 | EA | 1616
284 | 8 | UNLOADING of Conductor drums | Elecy | labour | SWR10509 | 100 | EA | 800
285 | 2 | Making of coil earthing pole with 8mm GI wireNut&Bolts for AB Switch AB Switch Coil Earthing GI No. 8 Wire | Elecy | labour | SWR12331 | 146.63 | EA | 293.26
286 | 6.4 | Fabrication of Main and Auxiliary structures with welding using raw steel such as RS joist, M.S.Angles, Plates, Channels, including the supply and fabrication of 6mm base plate to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection. | Elecy | labour | SWR10869 | 3426 | TO | 21926.4
287 | 100 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders) 12Mtrs/Spun Pole 0.92 M x 0.92M x 2.3M (3.0" x 3.0" x 7.6") Exc of Hard pit w/o blast 0.92X0.92X2.3M | Elecy | labour | SWR11041 | 1466.25 | EA | 146625
288 | 100 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation - Spun poles 12.5 Mtrs / 12.9Mtrs PSCC Erection of Spun pole 12.5Mt | Elecy | labour | SWR10350 | 4521.66 | EA | 452166
289 | 110.89 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Including the cost of cement | Elecy | labour | SWR10356 | 6579 | M3 | 729545.31
290 | 100 | LOADING of 12.5M SPUN POLE | Elecy | labour | SWR10190 | 548 | EA | 54800
291 | 100 | UNLOADING of 12.5M SPUN POLE | Elecy | labour | SWR10508 | 363 | EA | 36300
[7 empty] | sub Total | 16931945.756
11kv line labour
292 | 291 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders) 11 Mtrs PSCC Poles/ Box poles 0.75 M x 0.9 M x 1.95 M Ex of Hard pit w/o blast 0.75X0.9X1.95M | Elecy | labour | SWR11040 | 990.68 | EA | 288287.88
293 | 291 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation Errection of 11 M long PSCC pole | Elecy | labour | SWR10978 | 4336.85 | EA | 1262023.35
294 | 20 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rockboulders) 9.1 Mtrs PSCC Poles 0.76 M x 0.76M x 1.83M(2.6" x 2.6" x6.0") Exca Hard pit w/o blast 0.76X0.76X1.83M | Elecy | labour | SWR11039 | 928 | EA | 18560
295 | 20 | Erection of pole in position, aligning and setting to work, fixing of cross arms andtop clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation 9.1 M long PSCC poles for Strut Erec of 9.1 Mts PSCC poles for stuts | Elecy | labour | SWR11083 | 2400 | EA | 48000
296 | 291.228 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Including the cost of cement | Elecy | labour | SWR10356 | 6579 | M3 | 1915989.012
297 | 4 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders) 12Mtrs/Spun Pole 0.92 M x 0.92M x 2.3M (3.0" x 3.0" x 7.6") Exc of Hard pit w/o blast 0.92X0.92X2.3M | Elecy | labour | SWR11041 | 1466.25 | EA | 5865
298 | 4 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation. Erect-12Meter Box pole | Elecy | labour | SWR11267 | 3901.37 | EA | 15605.48
299 | 8 | Fabrication of 175x85/150x75mm RS joist pieces upto 12.5 meters length by welding joint together by means of 50x6mm flat and MS channel on either side including the cost of consumable. Fabrication of 175x85/150x75mm RS joist | Elecy | labour | SWR10642 | 512.55 | EA | 4100.4
300 | 8 | Painting of R.S Joist,Box poles including cross arms and clamps with one coat of red oxid and two coats of Al.paint including cost of paint and consumables Painting of RS Joist(1C RO, 2C Al.Paint) | Elecy | labour | SWR10640 | 1132 | EA | 9056
301 | 4.41 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Including the cost of cement | Elecy | labour | SWR10356 | 6579 | M3 | 29013.39
302 | 20 | Formation of Cut points Formation of Cut point for 11 KV Single Circuit line excluding pole erection and stays Formatn of Horiz Cut point for 11KV line | Elecy | labour | SWR10653 | 1435.81 | EA | 28716.2
303 | 2.45 | Fabrication & erection of Channels Fabrication of Main and Auxiliary structures with welding using raw steel such as RS joist, M.S.Angles, Plates, Channels, including the supply and fabrication of 6mm base plate to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection. Fabrication of struc.with welding. | Elecy | labour | SWR10869 | 3426 | TO | 8393.7
304 | 2.45 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. Sup Material for 1st coat Al. Painting. | Elecy | supply | SMR40009 | 2181 | TO | 5343.45
305 | 2.45 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium Labour for 1st coat Al. Painting. | Elecy | labour | SWR10877 | 851 | TO | 2084.95
306 | 2.45 | Painting of sub-station structures with two coats of Aluminium paint usingAluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2ndcoat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. Sup Material for 2nd coat Al. Painting. | Elecy | supply | SMR40010 | 1293 | TO | 3167.85
307 | 2.45 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium . Labour for 2nd coat Al. Painting. | Elecy | labour | SWR10879 | 482 | TO | 1180.9
308 | 5 | Paving out and stringing of conductor by providing temporary stays, tensioning, sagging correctly, fixing strain points, transferring to pin points binding, keeping stifner, rectification of poles, guys and jumpering etc., including transport of materialfrom road side to location. 55 Sqmm Single Circuit (3 Conductors) Stringing of 55sqmm 33/11kv Line 3 Cond | Elecy | labour | SWR10365 | 9454.81 | KM | 47274.05
309 | 940 | Excavation & laying of UG Cable (Double Run) Laying of XLPE UG cable Double Run including excavation of trench of size 600mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV from road level and cable separation with machine cut bricks horizontally for every 3 meters , providing of DWC/GI pipes wherever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and removing the debris from the site inluding the cost of lead and lift etc.. (Second cable laying cost not Included) depth of the trench LT-0.85 mts, Along the CC / BT multi layer road requiring compressor 33 KV 3x400 Sqmm Cable Lay-DR 33KV 3x400sqmm UG Cb CC/BT Compsr | Elecy | labour | SWR11980 | 1388.84 | M | 1305509.6
310 | 940 | Lay-2nd Cable in Excavated Trench | Elecy | labour | SWR10988 | 204.1 | M | 191854
311 | 120 | Excavation & laying of UG Cable in Single Run Laying of XLPE UG cable including excavation of trench of size 450mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV form road level,providing of DWC/GI pipes whereever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable,placing 40mm shabad protective slabs, back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc.depth of the trench) LT -0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs. Raising of cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required woodencleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe) 11 KV 3x300 Sqmm Cable Raise-SR 11KV 3x300sqmm UG Cb on support | Elecy | labour | SWR11955 | 144.08 | M | 17289.6
312 | 4 | Making 11 KV 3x300 Sqmm Cable Out Door/Indoor end termination OD/Idoor end termination 11kv 3x300 xlpe | Elecy | labour | SWR10391 | 2370.63 | EA | 9482.52
313 | 2 | UG Cables Joints : Straight through joint 11kv 3x300 xlpe | Elecy | labour | SWR10386 | 3725.45 | EA | 7450.9
314 | 5 | Stringing of HT AB Cable with GI Metal Parts HT AB Cable 11 KV 3x185+70 Sqmm Stringing of AB cbl 11 KV 3x185+70 Sqmm | Elecy | labour | SWR10454 | 41876.1 | KM | 209380.5
315 | 140 | Straight through joints of AB cable (each lead) Supply and ere Straight line Asmbly kits | Elecy | labour | SWR10672 | 1661 | EA | 232540
316 | 30 | Straight through joints of AB cable (each lead) Supply and ere Angle line Asmbly kits | Elecy | labour | SWR10673 | 2124 | EA | 63720
317 | 60 | End Termination of AB cable (each lead): Supply of 11KV 3x185+70sq.mm/ 3x70+70sq.mm/3x35+35sq.mm AB cable end Kits S-of 11KV AB cable end kits | Elecy | supply | SMR11504 | 950 | SET | 57000
318 | 60 | End Termination of AB cable (each lead): 120 Sqmm to 185 Sqmm End Termnatn of AB cable 120 to 185 Sqmm | Elecy | labour | SWR10667 | 800 | EA | 48000
319 | 10 | T Branch Kit S&Erect-T-Branch kit | Elecy | labour | SWR24971 | 3215 | EA | 32150
320 | 10 | T Branch Kit Erection of Assemble Kit for 'T' Branche | Elecy | labour | SWR10671 | 1800 | EA | 18000
321 | 166 | Supply and Erection of I Hook and Suspension Hook Supply- I Hook | Elecy | supply | SMR12099 | 158 | EA | 26228
322 | 166 | Supply and Erection of I Hook and Suspension Hook Erection- I Hook | Elecy | labour | SWR12099 | 55 | EA | 9130
323 | 60 | Supply of 120 Sqmm Aluminium lugs | Elecy | supply | SMR40132 | 12.52 | EA | 751.2
324 | 20 | Sub-transport of poles upto Workspot upto 10KM (Including loading and unloading) 9.1 Mtrs long PSCC Poles SubTrnsprt 9M PSCC Pole incl. L&UL<10KM | Elecy | labour | SWR20308 | 407.29 | EA | 8145.8
325 | 291 | Sub-transport of poles upto Workspot upto 10KM (Including loading and unloading) 11 Mtrs long PSCC Poles SubTrnsprt 11M PSCC Pole incl. L&UL<10KM | Elecy | labour | SWR11180 | 431.97 | EA | 125703.27
326 | 5 | Erection of 11KV 400/200A Conventional type AB Switch including fixing of cross angles and alignment complete | Elecy | labour | SWR10393 | 3200 | EA | 16000
327 | 5 | Painting of sub-station structures with two coats of Aluminium paint usingAluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2ndcoat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Painting of operating rods of 33kV, 11kV AB switches withpost office red colour (including cost of paint) Painting AB switch OP rods with PO red | Elecy | labour | SWR10881 | 142 | EA | 710
328 | 100 | Supply of earthing pipe with materials Supply of GI Flat 25X3 mm including material | Elecy | supply | SMR11485 | 105 | KG | 10500
329 | 2.45 | LOADING of MS Channel,Angles,Flats&Rods | Elecy | labour | SWR10206 | 221 | TO | 541.45
330 | 4.45 | Transport of steel including line materials such as cross arms, clamps, hardware, cable (loose) and other line materials (Including loading and unloading) TRANSPORT OF STEEL MATERIAL 20 TO 30KM | Elecy | labour | SWR10149 | 527.34 | TO | 2346.663
331 | 2.45 | UNLOADING of MS Channel,Angles,Flats&Rod | Elecy | labour | SWR10524 | 185 | TO | 453.25
332 | 10 | UNLOADING of 11 KV AB Cable (XLPE) 3 Core upto 500 Mts. Drum (including Accessories ) | Elecy | labour | SWR12431 | 438 | DR | 4380
333 | 10 | LOADING of 11 KV AB Cable (XLPE) 3 Core upto 500 Mts. Drum (including Accessories ) | Elecy | labour | SWR12413 | 584 | DR | 5840
334 | 375 | LOADING of 11kv Pin/Post/Solid Core Insulators | Elecy | labour | SWR10212 | 1 | CRT | 375
335 | 375 | UNLOADING of 33 & 11 KV Disc insulator | Elecy | labour | SWR10631 | 2 | CRT | 750
336 | 6 | LOADING of 11 KV Metal parts | Elecy | labour | SWR12402 | 48 | BAG | 288
337 | 6 | UNLOADING of 11 KV Metal parts Bag | Elecy | labour | SWR12421 | 48 | BAG | 288
338 | 9 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading) Note: 1). It will be treated as full load of 10 MT and paid for 10 MT. 2). For 3 Ton vehicle : 50% of the following rates Above 20 Km and upto 30 Km with Lorry for each trip Transport of Cond Drum,VCBs>20 & <30Km | Elecy | labour | SWR11862 | 3691.38 | EA | 33222.42
339 | 10 | Supply of Danger boards with clamps | Elecy | supply | SMR40070 | 116 | EA | 1160
340 | 15 | Supply of earthing pipe with materials S-CI Pipe earthing 50mm dia 2m long | Elecy | supply | SMR11484 | 2441 | EA | 36615
341 | 15 | Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50 M height ERECT. OF LINES-Providing of RCC collar | Elecy | labour | SWR10359 | 386 | EA | 5790
342 | 15 | Providing of earthing with excavation of earth pit (0.6 x0.6x2.4 Mts.) duly filling with bentonite, earth , running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.75M dia x 0.5 M height | Elecy | labour | SWR10357 | 1234.2 | EA | 18513
343 | 150 | Supply of earthing pipe with materials Supply of GI Flat 25X3 mm S-Earthing GI flat 25x3 mm incl material | Elecy | supply | SMR11485 | 105 | KG | 15750
344 | 4 | Load-11/33KV XLPE UG Cable for all sizes | Elecy | labour | SWR11230 | 1024 | DR | 4096
345 | 4 | Unload-11/33KV XLPE UG Cable all sizes | Elecy | labour | SWR11231 | 1024 | DR | 4096
346 | 8 | LOADING of R.S. Joists 175 x 85 mm | Elecy | labour | SWR10204 | 76 | EA | 608
347 | 8 | UNLOADING of R.S. Joists 175x 85 mm | Elecy | labour | SWR10522 | 50 | EA | 400
348 | 3 | LOADING of Conductor drums | Elecy | labour | SWR10191 | 202 | EA | 606
349 | 3 | UNLOADING of Conductor drums | Elecy | labour | SWR10509 | 100 | EA | 300
350 | 20 | Loading of PSCC Poles 9.1 M | Elecy | labour | swr10188 | 182 | EA | 3640
351 | 20 | Un loading of PSCC Poles 9.1 M | Elecy | labour | swr10506 | 91 | EA | 1820
352 | 291 | Loading of Spun poles 11.5 M | Elecy | labour | swr10189 | 440 | EA | 128040
353 | 291 | Un loading of PSCC Poles 9.1 M | Elecy | labour | swr10506 | 91 | EA | 26481
[7 empty] | sub Total | 6378606.785
Total Amount | [7 empty] | 27417011.4472
GST 18% | [7 empty] | 4935062.0605
Electrical total Amount | [7 empty] | 32352073.5077
WBS. No. S-1798-13-07-01-01-001(Civil)
1 | 32 | Leveliing the site by cutting and levelling with the help of JCB including cost,conveyance of all materials,hire chareges etc complete for finished item of work as directed by Engineer-in-charge. | Civil | Labour | SWR34179 | 2165 | Hrs | 69280
2 | 149.95 | Earth Work Mass Excavation (hard rock) to a depth as directed, in soils such as hard rock requiring blasting in prohibited area and all conditions such as dry, wet, slurry etc.and in dense or hard soils, disposal and depositing of excavated soil with intial lead of 10 mt and intial lift of 2m or as directed, including cost and conveyance of all materials, ramping and lifting of materials, and labour charges, hire charges of machinery, tools & plants, bailing of water ( either sub soil water, stoMts water, rain water, surface water or of any kind) if any at any stage of work until all works below ground level is finished to the satisfaction ,and from work such as shoring, timbering, strutting with required supports etc. for the work and removal of form work after completion of work etc all complete as directed by the engineer-incharge. | Civil | Labour | SWR33018 | 1440 | cum | 215928
3 | 115.65 | Earth work excavation in all type of soils red earth, Hard gravelly soils, earth mixed with sand and sandy soils etc., in all conditions such as slushy and dry with initial leads and lifts for foundations. Ordinary Soil | Civil | Labour | SWR33015 | 486 | cum | 56205.9 | Long text
4 | 22.79 | Plain Cement contrete (1:4:8) using 40 mm metal with concrete Mixture. All work upto Plinth level including cost and conveyance of all materials like cement, fine agregate (sand) coarse aggregate, water etc., to site and including Seigniorage changes, sales & other taxes on all materials including alol operational, incidental and labour charges such as machine mixing, laying concrete, curing etc., complete as directed by Engineer incharge of the work | Civil | Labour | SWR33028 | 4737 | cum | 107956.23 | Long text
5 | 108.3 | Coursed Rubble stone masonry 2nd sort with hard granite stones in cement mortar (1:6) for basement, including cost and conveyance of all materials, labour charges, curing, all leads and lifts, etc, complete for finished item of work. | Civil | Labour | SWR33041 | 4867 | cum | 527096.1
6 |  | RCC M20 Grade nominal mix using 12 to 20 mm HBG metal for following item of works including cost and conveyance of all materials labour scaffolding, centering, machine mixing, vibrating, curing all leads and lifts, in all positions of the building but excludi | [6 empty] | Long text
7 | 1.09 | RCC M20 Grade Footing | Civil | Labour | SWR33098 | 9488 | cum | 10341.92
8 | 1.58 | RCC M20 Grade Column | Civil | Labour | SWR33100 | 13237 | cum | 20914.46
9 | 1.15 | RCC M20 Grade plinth beam | Civil | Labour | SWR33099 | 12359 | cum | 14212.85
10 | 0.46 | Supplying, Cutting, bending, binding, placing in position and tying reinforcement steel in all heights including cost and conveyance of steel and binding wire etc,. With all leads and lifts, labour charges, etc., complete for finished item of work. | Civil | Labour | SWR33144 | 70687 | MT | 32516.02
11 | 66.71 | Brick masonry in cement mortar (1:6) for superstructure using well burnt country made second class bricks of approved quality including cost and conveyance of all materials curing, scaffolding with all leads and lifts in all heights etc., complete for finished item of work | Civil | Labour | SWR33068 | 8269 | cum | 551624.99 | Long text and amount
12 | 6.98 | Plain Cement concrete (1:2:4) using 20mm size well graded HBG metal for foundations, including cost, conveyance of all materials,labour all leads and lifts,consolidation and all operations, formwork as required, curing,etc. complete for finished item of work | Civil | Labour | SWR33030 | 6106 | cum | 42619.88
13 | 630.95 | Plastering with two coats, 1st coat in cm1:5 16mm thick and 2nd coat in cm 1:4 4mm thick, total 20mm thick for superstructure walls, ceiling, sunshades, Beams, etc., with sponge finishing including cost and conveyance of all materials all leads & lifts e | Civil | Labour | SWR33163 | 562 | Sqm | 354593.9 | Plastering with CM 2 coats, 20 mm thick, base coat in CM (1:6), 16 mm thick and top coat in CM (1:4), 4mm thick with Dubara sponze finishing including cost of all materials, seigniorage charges, excluding conveyance charges of materials and including all operational, incidental and labour charges for mixing mortar, laying rendering smooth and thread lining, curing, rounding off junctions of wall and slab etc., complete for finished item of work as directed by Engineer incharge of the work.
14 | 27 | Painting with two coats of ACE paint over a primary coat total three coats of approved colour and quality including cost and conveyance of all materials, labour charges etc., complete for finished item of work. | Civil | Labour | SWR33356 | 210 | Sqm | 5670
15 | 781.85 | Painting with two coats of Surya Cem paint over a primary coat total three coats of approved colour and quality including cost and conveyance of all materials, labour charges etc., complete for finished item of work. | Civil | Labour | SWR33329 | 85 | sqm | 66457.25
16 | 380 | Manufacturing, Supplying and fixing of MS grill for (Gate and raillings) of approved design as per drawings, including cost and conveyance of all materials, labour charges etc.,complete for finished item of work as directed by the Engineer- in-charge. | Civil | Labour | SWR33145 | 128 | Kgs | 48640
17 | 3 | Supply and Fixng of MS Name Board including cost & conveyance of all materials,labour charges etc complete for finished item of work. | Civil | Labour | SWR33421 | 4326 | sqm | 12978
18 | 1 | Geophysical Investgation charges for water point by Geologist | Civil | Labour | SWR33608 | 5000 | EA | 5000
19 |  | Drilling of 165mm bore well with machine rig including deployment and hire charges of rig and other machinery and equipment labour charges , measuring the yeild of borewell including cost and conveyance etc complete
20 | 90 | Drill-165mm Bore Well 0 to 90 | Civil | Labour | SWR33609 | 336 | M | 30240
21 | 30 | Drill-165mm Bore Well 90M to 120M | Civil | Labour | SWR34830 | 369 | M | 11070
22 | 30 | Drill-165mm Bore Well 120M to 150M | Civil | Labour | SWR34831 | 394 | M | 11820
23 | 30 | Drill-165mm Bore Well 150M to 180M | Civil | Labour | SWR34832 | 492 | M | 14760
24 | 30 | Drill-165mm Bore Well 180M to 210M | Civil | Labour | SWR34833 | 623 | M | 18690
25 | 30 | Drill-165mm Bore Well 210M to 240M | Civil | Labour | SWR34834 | 754 | M | 22620
26 | 30 | Drill-165mm Bore Well 240M to 270M | Civil | Labour | SWR34835 | 918 | M | 27540
27 | 90 | Drill-165mm Bore Well 270M and above | Civil | Labour | SWR34836 | 1082 | M | 97380
28 | 40 | Supply and fixing of 160mm dia PVC casing of A class 6Kg point pressure including cost and conveyance of all materials labour charges etc complete for finished item of work as directed by the engineer-in-charge. | Civil | Labour | SWR33611 | 883 | M | 35320
29 | 1 | Supply and erecting, ISI mark submersible 5.0 HP, Single Phase 30 stages pumpset suitable for 106/156mm dia borewell including cost and conveyance of all materials labour charges etc complete for finished item of work | Civil | Labour | SWR33640 | 48007 | EA | 48007
30 | 310 | Supply and fixing of HDPE pipe 40mm dia of 16Kg/cm2 including cost and conveyance of all materials labour charges etc complete for finished item of work as directed by the engineer-in-charge. | Civil | Labour | SWR34410 | 180 | M | 55800
31 | 1 | Supply and erecting D.O.L Starter 415V , Single phase,50Hz with SS enclouserincluding cost and conveyance of all materials labour charges etc complete for finished item of work | Civil | Labour | SWR33645 | 7854 | EA | 7854
32 | 315 | Supply of 3 Core 2.5 Sqmm Flat Copper cable of ISI for Submersible Motors of makes Finolex / Polycab / Gold Medal / Million / Payal / Sun Light / Power Flex / Fortune Art | Civil | Labour | SWR33641 | 192 | M | 60480
33 | 6 | Supply and Fixing of Ashirvad/ Ajay/ Astral Flowguard or equivalent CPVC Pipes and Fittings to meet the requirement of ASTM-D 2846 and are produced in CTS (Copper Tube Sizes 1/2" ton 2" Ashirvad Flowgurard SDR 11 and SDR 13.5 pipes are made from idential CPVC compounds having the same physical Properties for Hot and Cold Water (IS 15778:2007)-28.60mm OD Pipe - SDR 11 | Civil | Labour | SWR34363 | 410 | M | 2460
34 | 1 | Supply & fixing Gunmetal (GM) Ball valve with SS Ball and SS Spindle as per IS - Class - I, Indian make heavy type - 25mm NB Size | Civil | Labour | SWR34346 | 466 | EA | 466
35 | 64.95 | Earth work excavation in all type of soils red earth, Hard gravelly soils, earth mixed with sand and sandy soils etc., in all conditions such as slushy and dry with initial leads and lifts for foundations. | Civil | Labour | SWR33015 | 486 | Cum | 31565.7
36 | 13.54 | Plain Cement concrete (1:4:8) using 40mm HBG metal for foundations and leveling course, including cost and conveyance of all materials, labour all leads and lifts, consolidation and all operations, formwork as required, curing, etc. complete for finished item w | Civil | Labour | SWR33028 | 4737 | Cum | 64138.98
37 | 26.08 | Coursed Rubble stone masonry 2nd sort with hard granite stones in cement mortar (1:6) for basement, including cost and conveyance of all materials, labour charges, curing, all leads and lifts, etc, complete for finished item of work. | Civil | Labour | SWR33041 | 4867 | Cum | 126931.36
38 | 51.88 | Supplying and filling the substation site with borrowed gravel, watering, ramming, thoroughly complying with the standard specification. | Civil | Labour | SWR33052 | 309 | Cum | 16030.92
39 |  | RCC M20 Grade nominal mix using 12 to 20 mm HBG metal for following item of works including cost and conveyance of all materials labour scaffolding, centering, machine mixing, vibrating, curing all leads and lifts, in all positions of the building but excludi
40 | 3.56 | a) RCC M20 Grade Column Footings | Civil | Labour | SWR33098 | 9488 | Cum | 33777.28
41 | 2.28 | b)RCC M20 Grade Columns | Civil | Labour | SWR33100 | 13237 | Cum | 30180.36
42 | 2.25 | c)RCC M20 Grade Plinth Beams Long wall | Civil | Labour | SWR33099 | 12359 | Cum | 27807.75
43 | 3.17 | D) RCC M20 Grade Roof Beams landing beam | Civil | Labour | SWR33121 | 12275 | Cum | 38911.75
44 | 0.58 | e) RCC M20 Grade Lintels doors | Civil | Labour | SWR33107 | 13067 | Cum | 7578.86
45 | 2.7 | f) RCC M20 Grade Sunshades 600mm wide and 75mm thick | Civil | Labour | SWR33114 | 1375 | Sqm | 3712.5
46 | 15.22 | g) RCC M20 Grade Roof Slab for Control Room | Civil | Labour | SWR33128 | 10863 | Cum | 165334.86
47 | 3 | Supplying, Cutting, bending, binding, placing in position and tying reinforcement steel in all heights including cost and conveyance of steel and binding wire etc,. With all leads and lifts, labour charges, etc., complete for finished item of work. | Civil | Labour | SWR33144 | 70687 | MT | 212061
48 | 38.36 | Brick masonry in cement mortar (1:6) for superstructure using well burnt country made second class bricks of approved quality including cost and conveyance of all materials curing, scaffolding with all leads and lifts in all heights etc., complete for fin | Civil | Labour | SWR33068 | 8269 | Cum | 317198.84 | Long text
49 | 517.26 | Plastering with two coats, 1st coat in cm1:5 16mm thick and 2nd coat in cm 1:4 4mm thick, total 20mm thick for superstructure walls, ceiling, sunshades, Beams, etc., with sponge finishing including cost and conveyance of all materials all leads & lifts e | Civil | Labour | SWR33163 | 562 | Sqm | 290700.12 | Long text
50 | 16.56 | Providing Design R.C. drop wall of 25mm thickness with cm 1:3 and 6mm dia MS bars at 150mm both ways and chicken mesh in two coats 20mm thick each plastering including cost and conveyance of all materials with leads and lifts, scaffolding and curing, labo | Civil | Labour | SWR33203 | 3082 | Sqm | 51037.92
51 | 12.24 | Supply and fixing of Ms ornamental safety grill of approved design including cost and conveyance of all materials, labour charges etc., complete for finished item of work. | Civil | Labour | SWR33310 | 2990 | sqm | 36597.6
52 | 5.91 | Supply and fixing of doors with the frames of the door shall be made well seasoned mt wood of cross section 100x75mm. The shutter shall be made isi mark flushed door with decolam sheets pasted on both sides with PVC beading 40mm width all round.Frame shall be painted with two coats of synthetic enamel paint of approved color over one coat of primer over luppum with spary with 3 no 150mm brass hinges 1 no brass door stoper, 1 no 250mm brass aldrops. 2 no 300 mm aluminium tower bolts, 2 no 150mm brass fancy door handlers, 1 no keyless lockset with cp handel. The quoted rate shall include cost and conveyance of the meterials, fixig, labour carges, tools, handles,locking arrangementts and other fixtures & fittings for finished item work as directed by the Engineer - in- charge. | Civil | Labour | SWR33264 | 7314 | Sqm | 43225.74
53 | 20.25 | Raised pointing to the exposed surfaces of CRS masonry in cm 1:3 prop. including cost and conveyance of all materials, labour charges, all leads and lifts curing etc, complete for finished item of work. | Civil | Labour | SWR33184 | 125 | sqm | 2531.25
54 | 8.64 | Supplying and fixing Aluminium sliding windows with grill and fixed glass panels using anodised aluminium extruded sections of mat finish for frames and mullions made from approved aluminium sections 62x32x1.2mm at 0.73kg/Rm providing 5mm plain glass fix | Civil | Labour | SWR33277 | 3623 | sqm | 31302.72
55 | 16.56 | Supply and laying of Ceramic floor over of CM 1:3 20 mm thick including required materials and labour charges etc complete for item of work | Civil | Labour | SWR33224 | 914 | Sqm | 15135.84
56 | 121.92 | Flooring with double machine polished and hand cut Tandur blue stone 20mm thick of approved colour, quality and of minimum of 300x300mm size over a bed of cement mortar 1:3 20mm thick including cost of all materials, with all leads and lifts jointing and | Civil | Labour | SWR33219 | 787 | Sqm | 95951.04
57 | 6.74 | Supply and fixing of 4" high skirting of shabad stone to the walls including cost and conveyance of all materials, labour etc for finished item of work. | Civil | Labour | SWR33236 | 876 | Sqm | 5904.24
58 | 243.69 | Painting with two coats of OBD over a primary coat total three coats of approved colour and quality including cost and conveyance of all materials labour charges etc., complete for finished item of work. | Civil | Labour | SWR33333 | 146 | Sqm | 35578.74
59 | 349.52 | Painting with two coats of ACE paint over a primary coat total three coats of approved colour and quality including cost and conveyance of all materials, labour charges etc., complete for finished item of work. | Civil | Labour | SWR33356 | 210 | Sqm | 73399.2
60 | 101.17 | Providing impervious coat over RCC roof slab to requried slopes with 20mm thick in CM 1:3 mixed with approved brand of water proffing compound inclding cost and conveyance of all materials, labour charges, curing, rounding off junctions of wall and slab, all leads and lifts, etc . complete for finished item of work as directed by the Engineer - in - charge. | Civil | Labour | SWR33156 | 584 | sqm | 59083.28
61 | 60 | Supply & fixing of 25mm dia 2mm thick suSupply & fixing of 25mm dia 2mm thick surface P.V.C. pipe (ISI MARK) Concealed in wall with all required accessories including masonary work and labour charges etc.complete. | Civil | Labour | SWR33441 | 108 | Rmt | 6480
62 | 1 | Supply & fixing TPN Distribution board w Supply & fixing TPN Distribution board with IP-42 protection (Metal Door)suitable for 3 phase ELCB/RCCB/FP Isolator as incomer and 10kA SP MCBs as out going including internal connection and labour charges for surface / flush mounting etc Complete. | Civil | Labour | SWR33526 | 11353 | EA | 11353
63 | 10 | Supply & fixing of 6A 3 pin wall plug so Supply & fixing of 6A 3 pin wall plug socket with 6A switch control on a common switch board with earth continuity including wire leads,earth connection along with all labour charges etc., complete | Civil | Labour | SWR33468 | 166 | EA | 1660
64 | 6 | Supply & fixing of 16A 3 pin and 6A 3pin Supply & fixing of 16A 3 pin and 6A 3pin plug Flush type socket with indicator lamp and 16Amps fuse unit and 16Amps switch control (5 in one )duly recessed in wall with wooden deep box of 6'' x 8'' x 2 1/2'' size covered with hylam sheet earth connection and all labour charges etc., complete on wall. | Civil | Labour | SWR33470 | 449 | EA | 2694
65 | 24 | Wiring with 2 runs of 14/0.3mm (1.0 sq.m Wiring with 2 runs of 14/0.3mm (1.0 sq.mm)Fire Retardant (FR) P.V.C. insulated flexible copper cable (ISI MARK) in existing pipe with 6A Flush type Switch,ceiling rose and 3mm thick hylam sheet covering to switch control box including all labour charges etc., complete for light points, bell , fan and exhaust fan points in Non-Residential Buildings. | Civil | Labour | SWR33457 | 676 | EA | 16224
66 | 12 | Supply & Fixing of 28W T5 fluorescent tube. | Civil | Labour | SWR33558 | 148 | EA | 1776
67 | 1 | Supply of 12" (300mm)ISI, 900 RPM Heavy duty exhaust fan with metallic blades with Mark of makes Crompton / Bajaj / Havells / Orient. | Civil | Labour | SWR33571 | 2192 | EA | 2192
68 | 180 | Supply and run of 2 of 22/0.3mm (1.5 sq.mm) (FR) P.V.C. insulated flexible copper cable in existing pipe for mains including all labour charges complete. | Civil | Labour | SWR33496 | 75 | M | 13500
69 | 180 | Supply and run of 2 of 36/0.3mm (2.5 sq.mm) FR P.V.C. insulated flexible copper cable in existing pipe for mains including all labour charges complete. | Civil | Labour | SWR33497 | 103 | M | 18540
70 | 12 | Supply & fixing of batten holder /slanting holder in lieu of ceiling rose of light point complete with all connection and all labour charges with 40W bulb (for new installation). | Civil | Labour | SWR33484 | 141 | EA | 1692
71 | 4 | Supply & fixing of 1200mm (48'') sweep 230v,A.C 50 Hz.Ceiling fan with 3 Blades and double ball bearings with all standared accessories. | Civil | Labour | SWR33563 | 2277 | EA | 9108
72 | 4 | Supply & fixing of Electronic Regulator for ceiling fans 900/1200/1400mm sweep including cost of material, Electrical charges complete for finished item of work | Civil | Labour | SWR33564 | 589 | EA | 2356
73 | 1 | Providing independent EARTHING by excavating a trench to a depth of 2.1M in all solid,as per size specified in the Data,using 40mm dia 'B' class GI pipe of 2.5 Mtrs length with necessary accessories with hume pipe ring duly providing staggered holes including filling with equal proportion of salt and Charcoal in layers and all labour charges etc., compiete for small quarters. | Civil | Labour | SWR33596 | 5345 | EA | 5345
74 | 35 | Supplying, laying, jointing and testing 101.6 mm SWG SP-1 pipes of ISI make conforming to ISI 651 & 4127 with airtight cement joints in CM 1.5:1 prop. Including excavation of trenches and socket pits in any soil (except rock requiring blasting) up to 1524 mm(5'0") depth and refilling with watering and tamping. | Civil | Labour | SWR34281 | 755 | M | 26425
75 | 3 | Constructing 904.0 mm (3#0#) dia brick masonry inspection chamber as per IS - 4111: Part-1:1986 with cement mortar (1:6) prop using 2nd Class Clay Bricks of 225 mm thick from approved source having a minimum crushing strength of 5 N/sq.mm including plastering with cement mortar 1:3 prop; ½# thick both inside and outside fitted with 20# dia RCC manhole covers and frames including excavating pits up to a depth of 904 mm (3'-0") in all sorts of soils (excluding rock) and laying cement concrete (1:4:8) 150 mm thick using 40 mm HBG Metal and P.C.C. 1:2:4 benching and channel 100 mm thick as per Standard specification and including cost and conveyance of all materials like cement, sand, bricks, water etc., to site, cost of seigniorage charges on all materials and all incidental and operational, labour charges like mixing cement mortar, constructing masonry, lift charges, curing etc., complete for finished item of work as per Standard specification. | Civil | Labour | SWR34296 | 8766 | EA | 26298
76 | 4 | Supply & fixing of 110 mm dia - Door Bend 87.5 Degree - UPVC/SWR Pipe fittings (Prince/Sudhakar or any ISI Brand) | Civil | Labour | SWR34381 | 128 | EA | 512
77 | 4 | Supply & fixing of 110 mm dia - Plain Bend 87.5 Degree - UPVC/SWR Pipe fittings (Prince/Sudhakar or any ISI Brand) | Civil | Labour | SWR34380 | 100 | EA | 400
78 | 12 | Supply & fixing of 110 mm dia 3 M Single Socket PVC/SWR pipe - 6 Kg/sq.cm - Prince/Sudhakar or any ISI Brand | Civil | Labour | SWR34377 | 462 | M | 5544
79 | 18 | Supply & fixing of 90 mm dia 3 M Single Socket PVC/SWR pipe - 6 Kg/sq.cm - Prince/Sudhakar or any ISI Brand | Civil | Labour | SWR34378 | 410 | M | 7380
80 | 3 | Supplying & fixing 150 mm x 100 mm SWG gully traps conforming to ISI 651 & 4127 with C.I Grating & Cost. Brick masonry in CM 1:6 prop. Intermediate chamber and fitted with 304.8 mm x 288.6mm (12"x9") C.I Frame and hinged cover | Civil | Labour | SWR34286 | 767 | EA | 2301
81 | 1 | Supplying and Fixing of European Water Closet of 1st Quality | Civil | Labour | SWR34314 | 2228 | EA | 2228
82 | 6 | Supply & fixing 12.7 mm NP stop cock Indian make 400 grams Seiko/ Senior/ Nice/ Senior/ Nice or equivalent | Civil | Labour | SWR34328 | 721 | EA | 4326
83 | 4 | S&F 12.7 mm N.P bib tap Indian make 400 grams Seiko/ Senior/ Nice or equivalent | Civil | Labour | SWR34329 | 296 | EA | 1184
84 | 1 | Supplying & Fixing Indian make Flat Back Wash Hand Basin (HSW/Parryware/ Neycer) 1st quality conforming to IS:2556-Part-4:1972 with waste fittings like rubber plug, chain, 32 mm nominal size C.P. Fitting with parallel pipe thread conforming to IS:2963-1979 and fitted with 15 mm nominal bore Chromium Plated Pillar Tap of 1st quality Indian make 400 grams Seiko/ Senior/ Nice/ Esso or equivalent complete with standard CI brackets including wooden block: 550 x 400 mm - Single C.P. Pillar cock | Civil | Labour | SWR34316 | 1717 | EA | 1717
85 | 2 | Supply & fixing 38.1 mm C.P waste coupling Half or Full Thread 1st Quality Indian make Parryware or equivalent | Civil | Labour | SWR34428 | 309 | EA | 618
86 | 2 | Supply & fixing of 4" (101.6 mm ) Nahany Trap ( Without Jali with inlet)UPVC/SWR Pipe fittings (Prince/Sudhakar or any ISI Brand) | Civil | Labour | SWR34387 | 134 | EA | 268
87 | 1000 | Providing & Placing on Terrace (at all floor levels) polyethylene water storage tank with Double layer approved brand & manufacture with cover and suitable locking arrangement & making necessary holes for inlet & outlets and over flow pipes but with NECESSARY fittings & base support for tanks | Civil | Labour | SWR34375 | 10 | L | 10000
88 | 2 | Supply & fixing 31.75 mm dia PVC flexible waste pipe of 914.4 mm length of Ist quality | Civil | Labour | SWR34426 | 33 | EA | 66
89 | 45 | Supply and Fixing of Ashirvad/ Ajay/ Astral Flowguard or equivalent CPVC Pipes and Fittings to meet the requirement of ASTM-D 2846 and are produced in CTS (Copper Tube Sizes 1/2" ton 2" Ashirvad Flowgurard SDR 11 and SDR 13.5 pipes are made from idential CPVC compounds having the same physical Properties for Hot and Cold Water (IS 15778:2007)- 15.90mm OD Pipe - SDR 11 | Civil | Labour | SWR34361 | 239 | M | 10755
90 | 40 | Supply and Fixing of Ashirvad/ Ajay/ Astral Flowguard or equivalent CPVC Pipes and Fittings to meet the requirement of ASTM-D 2846 and are produced in CTS (Copper Tube Sizes 1/2" ton 2" Ashirvad Flowgurard SDR 11 and SDR 13.5 pipes are made from idential CPVC compounds having the same physical Properties for Hot and Cold Water (IS 15778:2007)-22.20mm OD Pipe - SDR 11 | Civil | Labour | SWR34362 | 313 | M | 12520
91 | 65 | Supply and Fixing of Ashirvad/ Ajay/ Astral Flowguard or equivalent CPVC Pipes and Fittings to meet the requirement of ASTM-D 2846 and are produced in CTS (Copper Tube Sizes 1/2" ton 2" Ashirvad Flowgurard SDR 11 and SDR 13.5 pipes are made from idential CPVC compounds having the same physical Properties for Hot and Cold Water (IS 15778:2007)-28.60mm OD Pipe - SDR 11 | Civil | Labour | SWR34363 | 410 | M | 26650
92 | 4 | Supply & fixing Gunmetal (GM) Ball valve with SS Ball and SS Spindle as per IS - Class - I, Indian make heavy type - 25mm NB Size | Civil | Labour | SWR34346 | 466 | EA | 1864
93 | 4 | Supply & fixing Gunmetal (GM) Ball valve with SS Ball and SS Spindle as per IS - Class - I, Indian make heavy type -20mm NB Size | Civil | Labour | SWR34345 | 331 | EA | 1324
94 | 1 | Supply & fixing 25.4 mm dia & 609.6 mm long aluminium anodized towel rod with brackets and aluminium screws | Civil | Labour | SWR34430 | 489 | EA | 489
95 | 85.51 | Earth work excavation in all type of soils red earth, Hard gravelly soils, earth mixed with sand and sandy soils etc., in all conditions such as slushy and dry with initial leads and lifts for foundations. Ordinary Soil | Civil | Labour | SWR33015 | 486 | cum | 41557.86
96 | 18.91 | Plain Cement concrete (1:4:8) using 40mm HBG metal for foundations and leveling course, including cost and conveyance of all materials, labour all leads and lifts, consolidation and all operations, formwork as required, curing, etc. complete for finished item w | Civil | Labour | SWR33028 | 4737 | cum | 89576.67
97 | 91.8 | Coursed Rubble stone masonry 2nd sort with hard granite stones in cement mortar (1:6) for basement, including cost and conveyance of all materials, labour charges, curing, all leads and lifts, etc, complete for finished item of work. | Civil | Labour | SWR33041 | 4867 | cum | 446790.6
98 | 36 | Plain Cement concrete (1:3:6) using 40mm HBG metal for foundations and leveling course, including cost and conveyance of all materials, labour all leads and lifts, consolidation and all operations, formwork as required, curing, etc. complete for finished item w | Civil | Labour | SWR33029 | 5027 | cum | 180972
99 | 108 | Raised pointing to the exposed surfaces of CRS masonry in cm 1:3 prop. including cost and conveyance of all materials, labour charges, all leads and lifts curing etc, complete for finished item of work. | Civil | Labour | SWR33184 | 125 | sq.mm | 13500
100 | 787.5 | Supplying and filling the substation site with borrowed gravel, watering, ramming, thoroughly complying with the standard specification. | Civil | Labour | SWR33052 | 309 | cum | 243337.5
101 | 88.8 | Plastering with two coats, 1st coat in cm1:5 16mm thick and 2nd coat in cm 1:4 4mm thick, total 20mm thick for superstructure walls, ceiling, sunshades, Beams, etc., with sponge finishing including cost and conveyance of all materials all leads & lifts e | Civil | Labour | SWR33163 | 562 | sq.mm | 49905.6
102 | 200.85 | Painting with two coats of Surya Cem paint over a primary coat total three coats of approved colour and quality including cost and conveyance of all materials, labour charges etc., complete for finished item of work. | Civil | Labour | SWR33329 | 85 | sq.mm | 17072.25
103 | 120 | Supply&Fabrication and fixing of Welded wire mesh ( 2" x 2") of 3mm dia. with ISMC (75x40x4.4mm) and Pheriperal frame of ISA(35x35x3mm) incldg cost& conveyance painting with synthetic enamil paint two coats over a coat of red oxide primer etc complete for finished item of work.. | Civil | Labour | SWR33403 | 2310 | sq.mm | 277200
104 | 160 | Supply and Fixing of Ashirvad/ Ajay/ Astral Flowguard or equivalent CPVC Pipes and Fittings to meet the requirement of ASTM-D 2846 and are produced in CTS (Copper Tube Sizes 1/2" ton 2" Ashirvad Flowgurard SDR 11 and SDR 13.5 pipes are made from idential CPVC compounds having the same physical Properties for Hot and Cold Water (IS 15778:2007)-22.20mm OD Pipe - SDR 11 | Civil | Labour | SWR34362 | 313 | rmt | 50080
105 | 30 | Supply & fixing Gunmetal (GM) Ball valve with SS Ball and SS Spindle as per IS - Class - I, Indian make heavy type - 25mm NB Size | Civil | Labour | SWR34346 | 466 | EA | 13980
106 | 1 | Providing Consultancy services for arranging contour surveying with total station incuding preparation of boundary and contour levels with 2 Nos. Hard copies and soft copies complete for finished items of work | Civil | Labour | SWR33427 | 5665 | EA | 5665
107 | 425.08 | Seigniorage Charges - Sand | Civil | Labour | SWR34470 | 40 | cum | 17003.2
108 | 1434.28 | Seigniorage Charges - Metal | Civil | Labour | SWR34471 | 97.5 | cum | 139842.3
109 | 839.38 | Seigniorage Charges - Gravel | Civil | Labour | SWR34472 | 30 | cum | 25181.4
110 | 60 | Supply and fixing of RCC fencing poles of size 0.1mx0.1mx1.8m (security fencing of sub station), including cost and conveyance of all labour, materials,and hire chareges etc complete for finished item of work. | Civil | Labour | SWR33405 | 1444 | EA | 86640
111 | 1200 | Supply and fixing of galvanised barded wire (1 horizantal & 2 cross strands. including cost and conveyance of all labour, materials,and hire chareges etc complete for finished item of work. | Civil | Labour | SWR33408 | 16 | M | 19200
[5 empty] | Total Rs. |  |  | 6355513.73
[5 empty] | 18% GST Rs. |  |  | 1143992.4714
[5 empty] | Grand Total Rs. |  |  | 7499506.2014
total Electrical+ civil schedule amount without GST | [7 empty] | 33772525.1772
with GST | [7 empty] | 39851579.7091