SOUTHERN POWER DISTRIBUTION COMPANY OF TELANGANA LIMITED, HYDERABAD

BID DOCUMENT

SPECIFICATION NO.: CE /O&M – 01/ 2024-25

REPAIRING/OVERHAULING OF SICK 33/11 KV POWER TRANSFORMERS

OF DIFFERENT MAKES AND VARIOUS CAPACITIES AVAILABLE AT VARIOUS SUBSTATIONS & SITES OF TGSPDCL ON RATE CONTRACT

PART-I

(TECHNICAL BID)

&

PART-II

(PRICE BID)

Phone: 040 – 23431380

040 – 23431496

Chief Engineer /O&M, TGSPDCL, 6-1-50, 5th Floor, A-Block,

Corporate office, Mint Compound,

Hyderabad -500 063

website: www.tgsouthernpower.org

|  | SOUTHERN POWER DISTRIBUTION COMPANY OF T.S. LTD 6-1-50, Corporate Office, Mint Compound, Hyderabad - 63 |
| --- | --- |

# e- Tendering Bid Notice (web Site)

Bids are invited through e-Tendering from the Eligible Local Bidders for REPAIRING/OVERHAULING OF SICK 33/11 KV POWER TRANSFORMERS OF DIFFERENT MAKES AND VARIOUS CAPACITIES AVAILABLE AT VARIOUS SUBSTATIONS AND SITES OF TGSPDCL ON RATE CONTRACT

The Bid document will be made available from 02.11.2024 from 11.00 Hrs and the last

date for submission of Bid is 29.11.2024  by 12.00 Hrs.

Further details of Bid Specification may be browsed from Web site of TGSPDCL www.tgsouthernpower.org &  www.tender.telangana.gov.in

Chief Engineer

Operation &Maintenance

TGSPDCL, Hyderabad.

Phone: 040 – 23431380

040 – 23431496

CONTENTS

Sl. No.                                 Title                                                         Page no.

- INVITATION FOR BIDS (IFB)                                 4-9

- SUMMARY SHEET                                                    10-11

- QUALIFICATION CRITERIA                                 12-13

- SECTION – 1 : GENERAL                                        14-25

- SECTION – 2 : FINANCIAL                                     26-30

- SECTION – 3 : TECHNICAL                                    31-36

7.	               FORM OF BID, BID SECURITY,		           37-54

PERFORMANCE   SECURITY,

SCHEDULES   A to N

8. 		    FORMAT-I & II                                                            55-65

NOTE:

- “Payment terms, Performance Bank Guarantee, Taxes and Duties” should be in line with the Terms and Conditions of the Bid specification. If any Bidder does not meet any one of the conditions, such Bid will not be considered.  Hence the Bidder shall submit the Bid in line with the Terms and Conditions of the Bid specification only.

- The Bidders shall check the website www.tgsouthernpower.org &         www.tender.telangana.gov.in for amendments, if any, up to one day prior to the date of Bid opening. The amendments shall be binding on the Bidders.

INVITATION FOR BIDS

SOUTHERN POWER DISTRIBUTION COMPANY OF TELANGANA LIMITED

MINT COMPOUND

HYDERABAD – 500 063

E-mail:-cgmoandmcpdcl@gmail.com

NOTICE for inviting the Bids for REPAIRING/OVERHAULING OF SICK 33/11 KV POWER TRANSFORMERS OF DIFFERENT MAKES AND VARIOUS CAPACITIES AVAILABLE AT VARIOUS SUBSTATIONS AND SITES OF TGSPDCL ON RATE CONTRACT

SPECIFICATION No: Chief Engineer/O&M: 01/2024-25

The Southern Power Distribution Company of Telangana Limited (TGSPDCL) is looking forward for REPAIRING/OVERHAULING OF SICK 33/11 KV POWER TRANSFORMERS OF DIFFERENT MAKES AND VARIOUS CAPACITIES AVAILABLE AT VARIOUS SUBSTATIONS AND SITES OF TGSPDCL ON RATE CONTRACT

In order to take up the above works, the T.G.S.P.D.C.L invites Bids from the eligible local bidders.

The various span of the Bidding process will be as per the following schedule:

| 1 | Downloading of Bid document | 02.11.2024, 11.00 Hrs onwards |
| --- | --- | --- |
| 2 | Opening of Bid | Technical Bid: 29.11.2024, 16.00 Hrs Price Bid: 07.12.2024, 15.00 Hrs |
| 3 | Bid cost | The interested Agencies and the Bidders may download the Tender Document from the web site www.tender.telangana.gov.in at free of cost. The transaction fee is to be paid as prescribed by M/s Vupadhi Techno Services Pvt. Ltd. |
| 4 | Bid security | Rs. 2,00,000/-(Rupees Two lakhs) (plus GST OF 18% applicable) in the form of Demand Draft drawn from any Nationalized Bank/ Scheduled Bank in favour of the Pay Officer/ TGSPDCL/ Hyderabad payable at Hyderabad or BG from Nationalized/ Scheduled Bank in favour of Chief Engineer/O&M/ TGSPDCL/ Hyd. |

Chief Engineer

Operation & Maintenance

TGSPDCL, Hyderabad

Guidelines for E-Tendering

The TGSPDCL is opting for e-tendering  for REPAIRING/OVERHAULING OF SICK 33/11 KV POWER TRANSFORMERS OF DIFFERENT MAKES AND VARIOUS CAPACITIES AVAILABLE AT VARIOUS SUBSTATIONS AND SITES OF TGSPDCL ON RATE CONTRACT

| Specification No. Chief Engineer/O&M: 01/2024-25 |  |  |  |
| --- | --- | --- | --- |
| Sl. No. | Description of Item | Date | Time |
|  | REPAIRING/OVERHAULING OF SICK 33/11 KV POWER TRANSFORMERS OF DIFFERENT MAKES AND VARIOUS CAPACITIES AVAILABLE AT VARIOUS SUBSTATIONS AND SITES OF TGSPDCL ON RATE CONTRACT |  |  |
| 1. | Schedule start date & time for downloading Bid document on e-procurement web site | 02.11.2024 | 11.00Hrs |
| 2. | Date of Pre-Bid meeting | 11.11.2024 | 11.00Hrs |
| 3. | Schedule end date & time for downloading Bid document on e-procurement web site | 29.11.2024 | 11.00Hrs |
| 4. | Bid Submission closing date & time on line | 29.11.2024 | 12.00Hrs |
| 5. | Last date & time for submission of hard copies along with DD | 29.11.2024 | 15.00Hrs |
| 6. | Technical Bid opening date & time | 29.11.2024 | 16.00Hrs |
| 7. | Date & time of Price Bid opening | 07.12.2024 | 15.00Hrs |

All the interested eligible local bidders may visit  www.tender.telangana.gov.in to view and download the Bid documents free-of-cost.

Those who are interested to submit Bids shall have to register in the above mentioned site and also have to obtain Digital Certificates. The details and procedure for obtaining digital certificate are mentioned in the website or contact the helpdesk of the site.

TGSPDCL

Specification No.Chief Engineer/O&M:  01/2024-25

Annexure

| Notice Inviting Bid Details |  |  |
| --- | --- | --- |
| Sl. No. | Description |  |
| 1 | Department Name | TGSPDCL |
| 2 | Office | Chief Engineer / O & M / TGSPDCL. |
| 3 | Bid Number | Specification No. CE/O&M: 01/2024-25 |
| 4 | Name of the Work | REPAIRING/OVERHAULING OF SICK 33/11 KV POWER TRANSFORMERS OF DIFFERENT MAKES AND VARIOUS CAPACITIES AVAILABLE AT VARIOUS SUBSTATIONS AND SITES OF TGSPDCL ON RATE CONTRACT |
| 5 | Work completion Schedule | According to terms & conditions |
| 6 | Type of Bid | e-tender |
| 7 | Bid Category | Open tender |
| 8 | Bid Security (INR) | Rs.2,00,000 /- (plus GST OF 18% applicable) |
| 9 | Bid Security Payable to | In the form of Demand Draft; shall be drawn from any Nationalized Bank/ Scheduled Bank in favour of the Pay Officer/TGSPDCL/ Hyderabad payable at Hyderabad or BG from Nationalized/ Scheduled Bank in favour of Chief Engineer/O&M/ TGSPDCL/Hyd. |
| 10 | Transaction Fee | Transaction Fee: All the participating Bidders who submit, have to pay an amount @ 0.03% of their final Bid value online a cap of Rs.10,000/- for quoted value of work up to Rs.50 Cores Rs. 25000/- if the purchase value is above Rs.50 crores & services applicable as levied by Govt. of India on transaction fee the online to the agency specified by TGTS department and the same amount is non refundable. Corpus Fund: Successful Bidder has to pay an amount of Rs. 4,000/- through demand draft in favour of Managing Director TSTS, Hyderabad towards corpus fund at the time of conclusion of agreement. |
| 11 | Transaction Fee Payable to | As specified by TGTS department |
| 12 | Bid submission closing date & time | 29.11.2024 at 12.00 Hrs for uploading 29.11.2024 at 15.00 Hrs for Hard copies |
| 13 | Bid Submission | On line |
| 14 | Technical Bid opening date & time | 29.11.2024 at 16.00 Hrs |
|  | Price Bid opening date & time | 07.12.2024 at 15.00 Hrs |
| 15 | Place of Tender Opening | Chief Engineer / O&M/ Corporate office / TGSPDCL/ Mint Compound, Hyderabad -500063 |
| 16 | Officer Inviting Bids/Contact Person | Chief Engineer / O&M/ Corporate office / TGSPDCL/ Mint Compound, Hyderabad -500063 |
| 17 | Address | O/o Chief Engineer/ O&M/ Corporate office / TGSPDCL/ Mint Compound, Hyderabad -500063 |
|  | E-mail Id | cgmoandmcpdcl@gmail.com |
| 18 | Contact Details/Telephone | Phone:040 – 23431380 040 – 23431496 |
| 19 | Procedure for Bid Submission | - Bids shall be submitted online on www.tender.telangana.gov.in platform. - The participating Bidders in the Bid should register themselves free of cost on e-procurement platform in the website www.tender.telangana.gov.in - Bidders can log-in to e-procurement platform in secure mode only by signing with the Digital certificates. - The eligible local Bidders who are desirous of participating in e-tendering shall submit their technical Bids, price Bids as per the standard formats available at the e-procurement platform. - The Bidders are requested to submit the documents as mentioned below: 6. The following Documents are to be uploaded on line as part of Technical bid & Price bid Sl. No.; Description. MANDATORY; 1; Financial Turnover: The Bidder should produce atleast Rs.25 lakhs turnover in any one financial year in the last preceding 5 years, certified by Chartered Accountant and shall submit Income Tax returns for previous consecutive 3 years.. 2; Copy of DD or BG for an amount of Rs 2,00,000/- towards Bid Security (plus GST OF 18% applicable).. 3; Physical Experience The eligible local bidder shall have a minimum period of 2 years experience in the field of repairing/manufacturing of power transformers and they should have repaired/ manufactured a minimum of 6 numbers power transformers of any capacities 33/11 KV class (3.15 MVA/5MVA/8MVA/12.5MVA/15MVA/ 16MVA), certified by not below the rank of Divisional Engineer or equivalent cadre of TRE wing.. 4; The repairer should have established workshop within the boundary of TGSPDCL, to accommodate and repair/ overhaul the Power Transformer and should have the essential equipment like (a)Heating chamber with Vacuum arrangement (b)At least 4 KL oil filtration plant (c)HV/LV coil winding machines(d)Insulating paper wrapping machine(e)40 tons overhead moving crane(f)Adequate testing facility to conduct all routine tests specified in IS–2026 shall be available and also capable of conducting heat run test on 33/11kV PTRs. The testing equipment should be calibrated by reputed agencies not prior to 1 year from the date of opening of bids and details of testing equipment should be submitted as per Schedule G of the tender specification. The bidders who do not possess above testing equipment properly calibrated by NABL will be treated as disqualified and their price bids will not be opened.. 5; The rates quoted should be within the range of -5% to +5% of schedule of rates. Bids received with rates quoted outside the above range will be rejected.. 6; The repairing shed shall be good enough to accommodate the allotted power transformers in a safer manner. The testing facility shall be in good condition & shall be at a convenient place to monitor the test results.. 7; Self declaration by the Bidder in token of having gone through carefully and thoroughly all the terms and conditions mentioned in the Bid document. 8; Financial Standing: The Bidder should produce details regarding Financial Standing as mentioned in Schedule-D. The minimum qualifying requirement is Rs.25 lakhs credit (or) Solvency & Such certificate should have been issued not earlier than six months prior to the date of Bid opening. Certificates from the bankers in proof of cash balance and other credit facilities shall be furnished in support without fail. The TGSPDCL reserves the right where ever necessary to make queries with the bidder’s bankers.. 9; Latest Income tax Return & Copy of PAN Card. 10; Copy of GST Registration. 11; Bid form. 12; All Schedules A to N. 13; Firm Registration/Registered Partnership deed in case of firm. 14; The repairing firms engaging the labour for PTR repairs are required to get registered with EPF & ESI. The Bidders should produce EPF &ESI registration certificates compulsorily along with latest challan details not earlier than 3/6 months paid towards their employees.. 7. For each uploaded document online, the Bidder should provide the index of the file names and its contents invariably. 8.Hard copies of uploaded documents along with DD/BG to be submitted as part of technical Bid and the hard copies are to be submitted before 29.11.2024,15.00hrs otherwise the Bid will be treated as non-responsive. 9. Any other documents as specified in the bid 10. The Department shall not hold any risk on account of postal delay; similarly, if any of the certificates, documents, etc., furnished by the Bidder are found to be misleading/false/fabricated/bogus, the Bidder will be disqualified and blacklisted duly forfeiting the Bid security. 11. The Department will not hold any risk and responsible regarding non-visibility of the scanned and uploaded documents. 12. Important Notice to Contractors, Suppliers Department users In the endeavor to bring total automation of processes e-Procurement, the Govt. has issued orders vide G.O.Ms.No.13 dated.5-07-2006 permitting integration of electronic Payment Gateway of ICICI/HDFC/IDBI/Axis Banks/Net banking with e-Procurement platform, which provides a facility to participating suppliers/contractors to electronically pay the transaction fee online using their credit cards. |
| 20 | Rights reserved with the Department | TGSPDCL reserves the right to accept or reject any or all the Bids received without assigning any reasons thereof. |

SUMMARY SHEET OF SPECIFICATION NO. : CE/O&M – 01/2024-25

| 1. | Description of work | : | Repairing/overhauling of 33/11 kV sick power transformers of various capacities (3.15 to 12.5/15/16 MVA) and of different makes, available at various substations/ sites of TGSPDCL on Rate Contract |
| --- | --- | --- | --- |
| 2. | Specification | : | E-procurement platform |
| 3. | Content of Specification | : | i) Invitation for Bids |
|  |  |  | ii) Summary sheet iii) Qualification Criteria |
|  |  |  | iv) Section 1 General |
|  |  |  | v) Section 2 Financial |
|  |  |  | vi) Section 3 Technical |
|  |  |  | vii) Form of bid, performance security, Schedules A to N |
| 4. | Officer to whom tender shall be addressed | : | Chief Engineer/O&M, TGSPDCL, 6-1-50, 5th Floor, A-Block, Corporate office, Mint Compound, Hyderabad-500 063. Phones : (040) 23431012, 23431380, 23431496 Email cgmoandmcpdcl@gmail.com |
| 5. | Date & time for Pre-Bid meeting | : | 11.11.2024 at 11.00Hrs |
| 6. | Superscription on the Pre-qualification bid cover having required hard copies along with DD/BG towards Bid Security | : | i) Name of the Bidder. |
|  |  |  | ii) Specification No. & Name of the work. |
|  |  |  | iii) Bid security enclosed in the form of Demand Draft/BG. No......... Dated ....... Amount:…. Name of the Bank:………… |
| 7. | Schedule start date & time for downloading Bid document on e-procurement web site | : | 02.11.2024 from 11.00Hrs. |
| 8. | Schedule end date & time for downloading Bid document on e-procurement web site |  | 29.11.2024 upto 11.00Hrs |
| 9. | Bid Submission closing date & time on line |  | 29.11.2024 at 12.00Hrs |
| 10. | Last date & time for submission of hard copies along with DD |  | 29.11.2024 at 15.00Hrs |
| 11. | Technical Bid opening date &time |  | 29.11.2024 at 16.00Hrs |
| 12. | Date & time of Price Bid opening |  | 07.12.2024 at 15.00Hrs |
| 13. | Place of Pre-Bid meeting and opening | : | O/o Chief Engineer /O&M, TGSPDCL, 6-1-50, 5th Floor, A-Block, Corporate office, Mint Compound, Hyderabad -500 063 |
| 14. | Performance Security to be paid. | : | 5% of the total value of the work either in the shape of DD/ BG at the time of entering into agreement (Para 2.3) |
| 15. | Bid Security Deposit | : | Rupees Two lakhs only (plus GST OF 18% applicable) |
| 16. | Validity of Bid | : | 90 days from the date of opening of Price Bid |
| 17. | Schedule of Delivery | : | The delivery period for any Unit shall not exceed 60 days for PTRs capacity upto 8 MVA and 90 days for PTRs of capacity above 8 MVA from the date of issuing of Job order |
| 18. | Terms and Conditions | : | Refer Sections 1 & 2 of specification. |
| 19. | Important Paras to be noted | : | Para 1.6, 1.9, 1.20, 1.24, 2.3, 2.4, 2.5, 2.6. |
|  |  | : | 1.1, 1.2.12, 1.7, 1.10.6, 1.12, 1.15.2, 1.16.8, 1.18, 1.19, 1.20, 1.21, 1.24.3, 1.25, 2.1, 2.1.4, 2.8. |
| 20. | Compulsory Enclosures to tender | : | - Bid form. - Schedule – A to N - All the required documents |
| 21. | Eligibility for Bidders. | : | - The eligible local bidder shall have a minimum period of 2 years experience in the field of repairing/ manufacturing of power transformers and they should have repaired/ manufactured a minimum of 6 numbers power transformers of any capacities 33/11 KV class (3.15 MVA/ 5MVA/8MVA/12.5MVA/15MVA/16MVA), certified by not below the rank of Divisional Engineer or equivalent cadre of TRE wing. - The repairer should have established workshop within the boundary of TGSPDCL, to accommodate and repair/ overhaul the Power Transformer and should have the essential equipment like Heating chamber with Vacuum arrangement, at least 4 KL oil filtration plant, HV/LV coil winding machines, Insulating paper wrapping machine, 40 tons overhead moving crane, adequate testing facility to conduct all routine tests specified in IS–2026 shall be available and also capable of conducting heat run test on 33/11kV PTRs. The testing equipment should be calibrated by NABL not prior to 1 year from the date of opening of bids and details of testing equipment should be submitted as per Schedule G of the tender specification. The bidders who do not possess above testing equipment properly calibrated by NABL will be treated as disqualified and their price bids will not be opened. - The new entrants for repair of Power Transformers must ensure that they possess the minimum qualifying requirements, except prescribed physical experience and should submit their offer accordingly. However, they have to possess the required infrastructure and if necessary, TGSPDCL officials will inspect the premises of the tenders to assess the capacity of the tenderer in repairing the Power Transformers. Initially, a PTR will be issued for repair and based on the performance, further allotment will be decided. The allotments of sick PTRs will be at the discretion of TGSPDCL & will be limited to maximum 10% of the average annual PTR failure. - (a) The rates quoted should be within the range of -5% to +5% of schedule of rates. Bids received with rates quoted outside the above range will be rejected. - (b) The repairing shed shall be good enough to accommodate the allotted power transformers in a safer manner. The testing facility shall be in good condition & shall be at a convenient place to monitor the test results. |

##### QUALIFICATION CRITERIA FOR THE BIDDER

- Physical Experience: The eligible local bidder shall have a minimum period of 2 years experience in the field of repairing/manufacturing of power transformers and they should have repaired/ manufactured a minimum of 6 numbers power transformers of any capacities 33/11 KV class (3.15 MVA/5MVA/8MVA/12.5MVA/15MVA/16MVA), which should be functioning satisfactorily atleast for a period of one year without any remarks after repairs/charging. The Bidder should furnish documentary evidence in support of the qualifying/experience requirements stipulated as above certified by an officer not below the rank of Divisional Engineer or equivalent cadre of TRE wing.

- The repairer should have established workshop within the boundary of TGSPDCL, to accommodate and repair/ overhaul the Power Transformer and should have the essential equipment like Heating chamber with Vacuum arrangement, at least 4 KL oil filtration plant, HV/LV coil winding machines, Insulating paper wrapping machine, 40 tons overhead moving crane, adequate testing facility to conduct all routine tests specified in IS–2026 shall be available and also capable of conducting heat run test on 33/11kV PTRs. The testing equipment should be calibrated by NABL not prior to 1 year from the date of opening of bids and details of testing equipment should be submitted as per Schedule G of the tender specification. The bidders who do not possess above testing equipment properly calibrated by NABL will be treated as disqualified and their price bids will not be opened.

- The new entrants for repair of Power Transformers must ensure that they possess the minimum qualifying requirements, except prescribed physical experience and should submit their offer accordingly. However, they have to possess the required infrastructure and if necessary, TGSPDCL officials will inspect the premises of the tenders to assess the capacity of the tenderer in repairing the Power Transformers. Initially, a PTR will be issued for repair and based on the performance, further allotment will be decided. The allotments of sick PTRs will be at the discretion of TGSPDCL & will be limited to maximum 10% of the average annual PTR failure.

- a) The rates quoted should be within the range of -5% to +5% of schedule of rates. Bids

received with rates quoted outside the above range will be rejected.

b) The repairing shed shall be good enough to accommodate the allotted power

transformers in a safer manner. The testing facility shall be in good condition & shall

be at a convenient place to monitor the test results.

- Sub-contractor’s experience will not be considered.

- Financial Turnover: The Bidder should produce atleast Rs.25 lakhs turnover in any one financial year in the last preceding 5 years, certified by Chartered Accountant and shall submit Income Tax returns for previous consecutive 3 years.

- Physical and Financial capacities of all the Bidders will be evaluated based on the documentary evidence furnished along with the bid separately. No correspondence will be entertained after opening of bids. Evaluation of Technical/Commercial and Price bids will be made based on the information evidence submitted by the Bidder along with the Bid only. Hence responsibility of correctness of the information submitted in Bid lies with the Bidder. If any information furnished in the bid is proved to be false at a later date, the bid will not only be rejected but the Bidder will be Black listed.

- Financial Standing:The Bidder should   produce details regarding Financial Standing as mentioned in Schedule-D. The minimum qualifying requirement is Rs.25 lakhs credit (or) Solvency & Such certificate should have been issued not earlier than six months prior to the date of Bid opening. Certificates from the bankers in proof of cash balance and other credit facilities shall be furnished in support without fail. The TGSPDCL reserves the right where ever necessary to make queries with the bidder’s bankers.

- The Bids not accompanying with the required documents such as Bid forms & schedule A- N will be treated as non-responsive and the price bids will not be opened.

- Pre-Qualification (Technical) bids opening: The Pre-Qualification bids will be opened on the date and time as specified. The agency should furnish all the original certificates to verify the documents/certificates submitted in the Pre-Qualification bid. The original certificates will be returned after verifying and tallying with the copies of certificates enclosed.

- Price-Bid opening: The price bids will be opened separately on the date and time specified.

- The repairing firms engaging the labour for PTR repairs are required to get registered with EPF & ESI. The Bidders should produce EPF & ESI registration certificates compulsorily along with latest challan details not earlier than 3/6 months paid towards their employees.

##### SECTION – I : GENERAL

  - Scope of Work:

    - The Southern Power Distribution Company of Telangana Limited hereinafter referred to as the TGSPDCL invites tenders to undertake repairing/overhauling to sick 33/11 kV Power Transformers of different makes and various capacities (3.15 to 12.5/15/16 MVA) available at various substations and sites of TGSPDCL from the eligible local bidders. This specification covers transportation, arranging for joint inspections, repairing/overhauling, testing and delivery at destination of sick 33/11 kV Power transformers. Rate contract will be entered into with eligible power transformers repairers. The rate contract will be for a period of two (2) years initially from the date of acceptance of the rates of TGSPDCL by the bidder.

    - The time of actual receipt in the office (indicated in the summary sheet) only will count for the acceptance of the tenders and not the date stamp of post office\courier services or the date stamp of any other office. TGSPDCL will not be responsible for any postal or any other transit delay.

1.1.3 	The Bidders are advised to check the website one day in advance of tender due date for any additions/modifications/omissions.

1.2	Filling up of Schedules:

    - All the schedules should be duly filled in but not necessarily be in the form sheets attached to the specification, but same Proforma has to be used if separate sheets are used. Unless full details required in the schedules are furnished, tender offers will not                                                               be considered.

    - All the required forms and documents shall be uploaded and hard copies of the same should be submitted before scheduled time.

    - The tender cover  shall be furnished  to the Chief Engineer/O&M, TGSPDCL,  6-1-50, 5th  Floor, A-Block, Corporate Office, Mint Compound, Hyderabad  500 063 before scheduled time.

    - In case any bid cover is received without having required documents, it will be liable for rejection.

    - Tenders will be opened at the time, date and place as specified.

    - The tenders will be opened in the presence of tenderers or their authorized representatives available at the time of opening of tenders.

    - All the folios of bids forms should be signed by the tenderer.

    - All the bids forms shall be uploaded and hard copies also shall be submitted.

    - Ambiguous and incomplete uploading of tenders will be rejected without assigning any reason.

    - TGSPDCL is not responsible for any delay or loss of tender specification sets during transit if sent by post or by any means.

    - TGSPDCL reserves the right to reject any tender or all tenders received without assigning any reasons.

    - The Telegraphic quotations will not be entertained under any circumstances.

  - Clearing Doubts:

    - Clarifications, amplifications, and/or any other correspondence from the tenderer subsequent to the opening of tender will not be entertained. The tenderers are therefore advised to ensure that their tenders are sent in complete shape in the first instance itself.

    - The Tenderers shall carefully examine the specification and all its enclosures and if the tenderer has any doubt about the meaning of any portion of this specification or schedules thereto, they shall obtain the required clarifications from the Chief Engineer /O&M/TGSPDCL in writing before 10 days of last date for receipts of bids. Verbal clarifications or information obtained by the tenderer shall not in any way binding on TGSPDCL.

  - Deviations from Specification:

    - No deviation from the terms and conditions are allowed. All tenders should strictly conform to the conditions notified. Any tender not in conformity with the notified conditions are liable to be rejected.

  - Due Date and Time for Uploading and Submission of Tender:

    - Tenders are to be uploaded in two parts

Part-I		-	Pre-qualification bid (Technical Bid)

Part-II		-	Price bid

1.5.2 The sealed cover in respect of the bid containing hard copies is to be submitted before the date and time as specified. The bidder must ensure that the following particulars are mentioned on the cover clearly.

i) Name of the Bidder.

ii) Specification No. & Name of the work.

iii) Bid security enclosed in the form of Demand Draft/Bank Guarantee No......... Dated ....... Amount:…. Name of the Bank:…………

    - Tenderer should upload the Technical bid and price bid.

    - The Tenderer should submit the sealed tender containing hard copies with the superscription on the envelope as specified in 1.5.2

    - The Tenderer shall invariably fill the forms and enclose the same to their bid.

- The date and time of closing the bid will be strictly adhered. No deviation or requests for other reasons will not be accepted.

- Tenderers are advised to ensure that their tenders are submitted in complete shape before closing date and time.

- Post tender rebates, revisions or deviation in quoted price and/or conditions or any such offers which will give benefit to the tenderer over others will not only be rejected outright but the original tender itself will get disqualified on this account and the Bid security (see para 1.6) will be forfeited

  - Bid Security/Earnest Money Deposit (EMD):

- The tenderer must pay an amount of Rs.2,00,000/- (Rupees Two lakhs only) (plus GST OF 18% applicable) towards Bid Security/EMD.

- The Bid Security/EMD shall be paid by way of crossed Demand Draft on State Bank of India or any other Scheduled Bank/ Nationalised Bank drawn in favour of the Pay Officer/TGSPDCL/Hyderabad payable at Hyderabad or BG from Nationalized/ Scheduled Bank in favour of Chief Engineer/O&M/ TGSPDCL/Hyd. The crossed demand draft shall compulsorily be enclosed along with other documents to be submitted in bid well before the date and time as specified.

- Submission of EMD by way of cheque, cash and money order will not be accepted and will be considered as disqualification.

- No interest shall be payable on Bid Security/EMD.

- Requests for exemption from payment of EMD will not be entertained in any case even though the tenderers are registered with DGS&D and NSIC.

- Manufacturers or power transformer repairers registered as SSI units with Industries Department, Government of Telangana are not exempted from payment of EMD , since the repair of power transformer is considered as work contract.

- The fact of having enclosed the EMD by way of Demand Draft/Bank Guarantee should be clearly superscribed on the sealed tender envelope as below:

Bid security enclosed in the form of Demand Draft./Bank Guarantee No.........  Dated

....... Amount:…. 	Name of the Bank:…………

- Tenders which do not contain the above superscription on the sealed envelop will be liable for rejection. TGSPDCL will not be responsible for any omission in this regard on the part of the tenderers which result in the return of the tenders unopened.

- Cases where the superscription is given on the cover but the Demand Draft is not found within, shall run the risk of being black listed by the TGSPDCL, in addition to rejection of their tender.

- The Bid security will be refunded to the unsuccessful tenderers on application after intimation to them that orders have been placed elsewhere. In the case of the successful tenderer or tenderers, the Bid security may be adjusted towards part of performance security deposit (see para 2.3) if the Bid security has been paid separately for this tender.

- The Bid security will be forfeited in the following cases.

- When a tenderer alters his price or withdraws his offer during the validity period.

- When the successful tenderer does not accept the order after issue of preliminary acceptance letter or the letter of intent.

- When the successful tenderer fails to furnish the performance security within 15 days from the date of issue of preliminary acceptance letter or the letter of intent (see para 2.3) for repairing a particular transformer.

- When a tender is disqualified for reasons outlined in para 1.5.5.

  - It is not binding on the TGSPDCL to accept the lowest or any tender. The TGSPDCL reserves the right to accept one or more tenders the rates quoted for items and /or to revise the agreement value to quicken the repair of sick power transformers as deemed necessary by the TGSPDCL. The TGSPDCL also reserves the right to accept or reject any particular tender without assigning any reason thereof.

  - Where a tenderer pleads his inability to undertake repairs to power transformers and backs out of his obligations after issue of the preliminary acceptance letter or the letter of Intent, the TGSPDCL/Hyderabad will forfeit his Performance Security and also recover the loss, if any, sustained by the TGSPDCL as a consequence of such backing out. In cases where the Performance security is not yet paid, the Bid Security will be forfeited and to make up the balance the security addition, the supplier firm will also become liable for being black listed.

  - Validity of Tender:

- Tender should be kept valid and open for acceptance for a period of not less than 90 days from the date of opening of the Price bid. The period of validity cannot be from any date other than the date of opening of Price bid. The tenderers will not be permitted to withdraw or vary their offers after the date of opening of the tenders and if they do so, the EMD will be forfeited.

- Tenderers giving validity of less than 90 days are liable to be rejected and returned unopened at the discretion of TGSPDCL.

  - Past Performance:

- Only manufacturers/repairers of power transformers who qualify as per the pre-qualification requirement must quote. Tenders received from Agents/Dealers/Sub-Contractors will not be considered.

- TGSPDCL reserves the right to reject any bid/bids on account of past performance in the earlier awarded works at any stage of evaluation of bids. If any bid is rejected at technical evaluation stage, its price bid will not be opened.

- The new entrants for repair of Power Transformers must ensure that they possess the minimum qualifying requirements, except prescribed physical experience and should submit their offer accordingly. However, they have to possess the required infrastructure and if necessary, TGSPDCL officials will inspect the premises of the tenders to assess the capacity of the tenderer in repairing the Power Transformers.

Initially, a PTR will be issued for repair and based on the performance, further allotment will be decided. The allotments of sick PTRs will be at the discretion of TGSPDCL & will be limited to maximum 10% of the average annual PTR failure.

- The tenderer should invariably enclose the audited balance sheet for the previous financial year.

- The tenderer should furnish full particulars regarding past performance on repairs of power transformers to TGSPDCL or other Discoms/TSTRANSCO and other organizations. The information shall be filled up in the Proforma i.e., enclosed to this specification (Schedule-H & Schedule-I).

- The Price bids of the tenderers who do not qualify with the minimum qualification requirements i.e., relevant experience, infrastructure, minimum machinery, testing equipment, etc., will not be opened.

- While being equal or comparable in other aspects preference will be given to those tenderers who have experience in manufacture and repair of power transformers similar to that given in specification or of higher ratings during last three years, at the sole discretion of the TGSPDCL.

  - Tax Clearance Certificates:

- The tenderer shall enclose copies of Income Tax, Sales Tax and Turnover Tax certificates from the appropriate Income tax authority on the form prescribed thereof. In the case of proprietary or partnership firm it will be necessary to produce the certificate/certificates for the proprietor or proprietors and for each of the partners as the case may be. If the certificate had already been produced by the tenderer during the calendar year in which the tender is made, it will be sufficient if particulars of the previous occasion are given.

  - Acceptance:

    - The successful tenderer(s) will be accepted by the TGSPDCL to undertake repair work to the sick Power Transformers at the rates quoted by the tenderer and approved by the TGSPDCL for a period of two years subject to periodic review of the quality and progress of repair work by the TGSPDCL. The progress of work will also be monitored by TGSPDCL through a Web Tracking system called OTPR (Optimization of Turn around time of PTR Repairs) as per Schedule-N.

    - The rates quoted against this specification or the accepted rates communicated shall be valid and in force upto 2 years from the date of issue of acceptance letters. The sick Power Transformers allotted during the above 2 years and including on last day of the rate contract period shall be covered by the rates accepted and communicated as per this specification.

    - The successful tenderer(s) shall contact the Superintending Engineer of Operation/SCADA circle as indicated in the letter of allotment and take over the sick power transformers after furnishing the Bid Security and additional security as per the contract terms and enter into agreement with the concerned Superintending Engineer/ Operation/SCADA within 15 days from the date of issue of letter of allotment by the Chief Engineer/O&M/TGSPDCL/ Hyderabad.

    - If the successful tenderer(s) has been allotted the repairs of sick Power Transformer units belonging to the different Superintending Engineers of Operation/ SCADA circles under TGSPDCL, the successful tenderer shall enter into separate agreements with each one of them as per para 1.12.3. Further repair works will be allotted by the Chief Engineer/O&M/TGSPDCL/ Hyderabad during the contract period progressively on completion of works on hand.

    - The TGSPDCL reserves the right to supply winding conductors, Transformer Oil, Bushing and other parts to the successful tenderer(s) at its discretion for replacement in the sick units handed over for repair work to the tenderer. In such cases price quoted for replacement of such items shall not be payable to the tenderer. This shall not in any way affect Guarantee and workmanship of the works executed by the successful tenderer(s) against the contract and shall not vary the overall nature of the contract.

    - The TGSPDCL reserves the right to terminate the agreement if the quality and progress of repair work is not satisfactory.

    - The TGSPDCL reserves the right to extend the period of agreement by one more year beyond two years based on performance of the contract by the tenderer during the agreement period.

    - The sick power transformer units spread over in various SPM centres, substations and other sites of TGSPDCL the transformer units will be handed over either where they are or at the repair centres of the successful tenderer(S) at the discretion of TGSPDCL. In case the transformers are handed over where they are with TGSPDCL, the transport shall be arranged by the successful tenderers at approved scheduled rates of TGSPDCL and the cost shall be borne by the TGSPDCL.

  - Service Conditions:

- The repaired power transformers will operate under the following tropical conditions.

i) 	Maximum Humidity		-	100%

ii) 	Maximum isokeraunic level	-	50 thunderstorm days

iii) 	Maximum temperature in shade	-	50 to 45 deg. C

iv) 	Minimum temperature in shade	-	7.5 deg. C

v) 	Maximum temperature on sun	-	70 deg. C

vi) 	Altitude above sea level		-	up to 1000 meters

  - Due consideration will be given to any special devices or attachments, put forward by the tenderer which are calculated to enhance the general utility, safe and efficient operation of the Power Transformers.

  - Completeness of Tender:

- The tender should be complete with all details of materials, illustrative and descriptive literature and drawings, and information regarding materials used in the repairing of Power Transformer. Tenders not accompanied by this information are liable for rejection.

- The tender should include all minor accessories not specifically mentioned in this specification but essential for the completeness of the Power Transformer repair/overhaul. The tenderer shall not be eligible for any extra charges in respect of such minor accessories, even though they are not mentioned in the tender specification.

  - Allotment of sick Power Transformer:

    - The TGSPDCL reserves the right to allot the work to more than one repairer at the same rates in view of urgency who have participated in the tender and come forward to undertake the repairs at the lowest rates / negotiated rates.

    - After confirming by TGSPDCL the acceptance of rates, sick Power Transformer will be allotted among all the rate contract holders on rotation basis, subject to number of pending Works/Jobs on hand among the repairers at the time of allotment of further sick PTR i.e. the repairer with minimum no. of pending Jobs on hand and the agency which has got less RGP failures will get priority for allotment of sick PTR.

    - The local SSI units situated in TGSPDCL jurisdiction will be given preference in allotment of the Power Transformers.

    - Proximity of the firm from the location of the sick power Transformer will be considered in awarding the work to minimize the transportation charges.

    - The second Power Transformer shall be allotted after handing over the first allotted repaired/overhauled Power Transformer.

    - The subsequent allotment of sick Power Transformers will be based on the performance of the Power Transformers repaired by each company/firm.

    - It is the sole discretion of TGSPDCL to allot the sick Power Transformers to any bidder/repairer; mere eligibility does not automatically entitle any rights on any bidder for award of repair work.

    - The repairer shall lift the sick power transformer within 7 days of intimation of fixing of agency. If there is any delay beyond 7 days, the agency shall be skipped for the allotments from the regular cycle.

  - Joint Inspection:

    - The repairer shall inform the receipt of sick Power Transformer to their shed immediately to the Chief Engineer/O&M/TGSPDCL, Superintending Engineer/ Operation/SCADA circle, DE/Transformers and Second inspecting officer for conducting joint inspection for assessing the extent of damages.

    - The successful tenderer who will be allotted the sick power transformers for repairs shall arrange for joint inspection with the authorized representative of the TGSPDCL within one week of the receipt of the failed power transformers at the repairer’s shed to evaluate the damages to the sick Power Transformer and to record pre-measurements of the damages and assessment of repair work to be carried out.

    - The delivery period for any sick unit shall not exceed 60 days for PTRs of capacity upto 8 MVA and 90 days for PTRs of capacity above 8 MVA, from the date of issuing of Job order for repair/overhaul of Power Transformer.

    - After conducting joint inspection, the prescribed Joint Inspection report i.e. Format-I will be uploaded in the OTPR website by the repairer within 24 Hours of Joint inspection and the same is to be authorized by the concerned DE/TRE within 3 days and the estimate will be scrutinized, processed. If found reasonable, orders for repairing/overhauling the Power Transformer will be placed.

    - After Joint Inspection if the repairs are uneconomical TGSPDCL will cancel the allotment.

    - If the Contractor/Repairer does not show the progress as per the time schedule i.e. the prescribed time schedule which is monitored through OTPR (Schedule-N), TGSPDCL reserves the right to cancel the work. Such work(s) may be got executed through alternative agencies at Contractor’s cost and risk; and without prejudice to the right of the TGSPDCL to levy any penalties as per the terms of the agreement.

  - TGSPDCL Hold Quality plan on Stage wise Inspections:

  - Stage wise inspection of LV winding and HV winding shall be arranged in the presence of TGSPDCL joint inspecting officer before Core Coil Assembly to ensure that the repair/overhaul works have been carried as per the Joint Inspection report and to check all items as per repair/overhaul estimate. This is TGSPDCL hold point (Customer Hold Quality plan CHQ) and without TGSPDCL approval of clearance at this stage the repair/overhaul work of sick Power Transformer shall not be carried for the next stage. Second inspection notes (Ensuring weights of winding according to issued Job order) along with photos are to be uploaded in web for carrying out further repair work.

  - The repairer shall invite for inspection after CCA and inspection notes shall be prepared in the presence of repairer's representative and TGSPDCL's representatives.

  - Testing and Inspections:

    - The power transformers after repair shall be tested in the presence of Joint Inspecting Officer as stipulated in the specification and as per relevant ISS and the test certificates (in the format mentioned in  Schedule-G attached to tender specification) witnessed and approved by concerned DE/TRE of the circle duly ensuring the NABL certification should be submitted to Corporate Office. The Tenderer should specifically mention Schedule G about furnishing the test certificates of the testing equipment in the above mentioned format which is uniquely designed for this purpose and it should be followed scrupulously. The final test report of repaired PTR in a prescribed format i.e. Format-II is to be uploaded in web along with test certificates of the equipment utilized for testing of PTR at the agency. Also the DE/TRE of concerned circle is to witness the final testing of repaired PTR & upload the documents.

    - The accredited representative of the TGSPDCL /Hyderabad shall have access to the works of the successful tenderer (s) at any time during the working hours for the purpose of inspection during the repairing of equipment and testing. The tenderer should provide all the facilities for testing at any time. As soon as the repaired equipment is ready the tenderer should duly send intimation to the concerned Superintending Engineer/ Operation/SCADA circle of TGSPDCL with a copy to the Chief Engineer/O&M/ TGSPDCL by Regd. post and carry out the tests before the representatives of TGSPDCL.

    - The dispatches shall be affected only if the test results comply with the relevant IS specification. The dispatch shall be made only after the inspection by the TGSPDCL Officer is completed to his satisfaction and the Inspecting Officer gives clearance for the repaired/overhauled unit to move to the destination station. If the test results are found to be not satisfactory, the repairer has to make further necessary repairs to the Power Transformer till the test results are satisfactory.

    - Expenditure towards testing is to the account of repairer only.

- Delivery:

    - The delivery period shall be reckoned from the date of placing repair/overhaul orders and delivery period is 60 days for PTRs of capacity upto 8 MVA and 90 days for PTRs of capacity above 8 MVA. The delivery period  shall be firm, definite, unconditional and on the basis of receipt of repaired units at destination in good condition without any bearing on the procurement of raw material or any similar prerequisites. The repairer should take care of all the delivery periods for material procurements.

    - The repairer shall adhere to the delivery period as specified at 1.17.3, failing which the penalty shall be levied as per para 1.21 below.

    - The successful tenderer will not be normally permitted to carryout repairs for more than '2' (two) sick units of TGSPDCL at any one time and shall be capable of delivering at the rate of one unit per month. The delivery period for any unit shall not exceed 60 days for PTRs of capacity upto 8 MVA and 90 days for PTRs of capacity above 8 MVA, from the date of issuing of Job order for repair/overhaul of Power Transformer. The delivery period for each sick unit against the contract shall be guaranteed under penalty as in Para 1.21. TGSPDCL reserves the right to revise the delivery destination before completion of inspection and testing without any change in terms and conditions. The period of delay on the part of the TGSPDCL to communicate the delivery destination by the time of final inspection and testing, shall not be counted for penalty under Para 1.21.

    - The date of delivery is the date on which the transformer is notified as being ready for testing/dispatch after repair/overhaul (in the absence of such notification, the date of dispatch Transport Note is to be considered as the date of delivery) or the contracted delivery date (including any agreed extension thereto), whichever is earlier.

- Penalty and Late Delivery:

    - a) In case of delay in delivery of BGP/ overhauling PTRs, whatever be the reasons, the TGSPDCL may at its option demand and recover an amount equivalent to 0.5 percent of value of the estimated /actual repair cost, whichever is higher for every week of delay or part thereof subject to a maximum of 5% of total value of the contract. The right of TGSPDCL shall be without prejudice to its rights under the law including the right to cancel the contract, forfeit deposit and /or recover damages for breach of contract.

    - b) In case of delay in delivery of RGP PTRs beyond the scheduled period of 52 days i.e. PTR shall be lifted by the repairer within 7 days of intimation by TGSPDCL officers and the same shall be repaired/ replaced and delivered within 45 days after receiving the unit, whatever be the reasons, the TGSPDCL may at its option demand and recover an amount equivalent to 1% of performance security deposit/ bid security amount, whichever is higher, for every 10 days of delay in delivery.

    - c) If the unit is still not repaired beyond 120 days for BGP failed PTR and 75 days for RGP failed PTR, in addition to above mentioned clauses (a) & (b), further repair works will not be allotted till pending PTRs for repairs are completed & kept ready for dispatch.

- Materials & Workmanship:

    - The workmanship shall be of the highest grade and the entire repair shall be in accordance with the best modern practice and in conformity with the IS and CBIP specifications.

    - All the materials used in the repair/overhaul of Power Transformer shall be of the best class and shall be capable of satisfactory operation in the tropics under service conditions without distortion or deterioration. They shall confirm to the requirements of the appropriate Indian Standards. If the material used is not as per standards then the repairer/contractor will be black listed and amounts will not be paid to him.

    - The entire design and construction shall be capable of withstanding the severest stresses likely to occur in actual service and of resisting rough handling during transport.

    - The TGSPDCL reserves the right to order for 3rd party inspection of the materials supplied and utilized by the contractor for the repair/overhaul for its quality and performance.

    - All works shall be carried out in accordance with the relevant clauses of the Indian Electricity Act and Rules unless modified by this specification. In case of variation between the two, the later shall be binding on the repairer.

- Packing:

- The equipment and all its accessories shall be securely packed and dispatched at contractor’s/Repairer’s risk and cost. The packing maybe in accordance with the manufacturer’s standard practice unless otherwise specified. The Contractor/Repairer should however, ensure that the packing is such that equipments reach the destination without damages after transport by Road. Any material found short inside the intact packing cases shall be supplied by the contractor at no extra cost to the TGSPDCL including freight charges.

- Guarantee:

- The successful Tenderer shall guarantee the repaired/overhauled power transformer units as follows:

- Safe electrical and mechanical stresses on all parts of the equipment, under specified conditions of operation.

- Quality and strength of materials

- The repaired/overhauled PTR shall be guaranteed for satisfactory operation for a period of atleast one and half year (18 months) from the date of commissioning for failed locations & from the date of receipt at Substation location for New SS/Works. The receipt of the PTR details must be uploaded in SAP by DE/TRE concerned soon after receiving the PTR.

- If during the period of guarantee, the repaired/overhauled PTR is found defective and /or fail in test or while in operation, such PTR shall be lifted by the repairer within 7 days of intimation by TGSPDCL officers and the same shall be repaired/ replaced and delivered within 45 days after receiving the unit, at free of cost including loading, unloading and to and fro transport charges of failed/repaired PTR under RGP, irrespective of the reimbursements from the insurance company, failing which the unit will be taken back and repairing cost will have to borne by the repairer. In case, the unit cannot be taken back by TGSPDCL, the cost of the failed units will be deducted from subsequent bills/bank guarantee.

- The Repairing Agency shall call for inspection for assessment of damages, Stage wise inspection during repairs and for final Testing by concerned DE/TRE. The same shall be submitted by DE/TRE to CE/O&M.

- If the repair job fails twice within the Repair Guarantee Period, the allotment of PTR in cyclic order will be withheld for six months and if the repair job fails thrice within the RGP, the firm will be removed from the approved repairers list. The re-repaired transformer units shall be guaranteed for at least one year or for the un-expired portion of the guarantee period from the date of re-commissioning of the unit, whichever is higher. After repairs the PTR has to be transported to the place allotted.

- No fresh oil shall be issued by TGSPDCL for the power transformers failed under 	Repair  Guarantee Period (RGP) .The oil filled for tanking of PTRs failed under RGP shall be properly filtered and carry the satisfactory levels of breakdown values. Oil testing report shall be submitted.

- Jurisdiction:

    - All and any disputes or differences arising out of or touching the order against this specification shall be decided only by a panel of arbitrators as detailed below:

| i) Disputes involving amounts upto and below Rs.10,000/- | The Superintending Engineer/ Operation of the TGSPDCL other than the circle to which the dispute relates. |
| --- | --- |
| ii) Disputes involving amounts ranging from Rs.10,001/- to Rs.50,000/- | The Chief Engineer/O&M of the TGSPDCL. |

There shall not be any reference of disputes to the arbitration, if the value is above Rs.50,000/-.

    - The parties shall approach the competent Civil Courts (situated at Hyderabad and Secunderabad only), if any such disputes arise and where the value is more than Rs.50,000/-.

- Works to be allotted on trial basis:

  - To encourage and develop new vendors and to have more sources, trial orders can be considered where the price offered by the technically acceptable bidder is lower than that of the technically acceptable regular contractor. Where the bidder is a regular contractor to other electricity utilities / corporations / public sector undertakings during the past 3 or 4 years and its performance is proven, it can be considered for trial orders subject to its offer being technically acceptable.

  - The total orders will be limited to a maximum quantity of 10% of the average annual requirement. When a trial order is placed the same will be brought to the notice of the receiving officer for early installation of the equipment/ material, monitoring of performance and reporting its performance.

  - Trial Orders can be placed on Bidders whose bids are technically qualified only.

  - However, for placing the trial orders their quoted price shall be lower at least 5 % of the L1 price (which is technically & commercial qualified).Apart from this , the Bidder seeking Trial Order shall pass on any advantage on account of the duties & taxes to TGSPDCL.

  - Statutory Obligations:

    - The Contractor shall take all steps as may be necessary to comply with the various applicable laws/rules including the provisions of contract labour (Regulation & Abolition Act) 1970 as amended, minimum wages Act, 1984, Workman Compensation Act, ESI Act, PF Act, Bonus Act and all other applicable laws and rules framed there under including any statutory approval required from the Central/State Govt. Ministry of Labour. The Contractor should obtain the above documents and submit the same to the Engineer-incharge before commencement of work.

  - Human Resource Issues:

    - The CONTRACTOR would execute these works through their own resources.

    - The CONTRACTOR shall bear all expenses/cost to be incurred towards salary, allowances, perks, traveling allowances, advances, insurance, safety measures, security, transportation and all other misc. expenses etc. of their employees/ workmen during the tenure of AMC. Also, the CONTRACTOR shall be sole responsible for making payment for Hospitalization, Compensation thereof in case of any accident & injury.

    - The CONTRACTOR shall issue Identity Cards to their employees deployed for execution of the assigned works in the District with the consent of Engineer Incharge.

    - The CONTRACTOR to deploy their manpower immediately for carrying out the work specified above.

    - The CONTRACTOR should ensure that there are no disputes regarding service, payment etc of the persons engaged by him, anytime during the currency of the contract. At no point of time during the currency of contract, the CONTRACTOR's employees shall insist upon the COMPANY for employment, wages, and allowances or any other related matter, payment etc.

    - The CONTRACTOR shall not deploy the manpower below the age of 18 years and above 58 yrs.

    - The CONTRACTOR shall not deploy the female manpower between 7 PM to 6 AM.

    - The CONTRACTOR shall be directly responsible for any / all disputes arising between him and his persons and keep the COMPANY indemnified against all losses, damages and claims arising thereof. The CONTRACTOR shall resolve any dispute of their manpower. All the legal dues of their manpower is to be paid on due date or within 8 days on the termination of manpower.

    - All safety wears required for the CONTRACTOR's manpower during the execution of work such as safety shoes, safety helmets, hand gloves, safety belt, dust mask, goggles etc. must be provided by the CONTRACTOR at his own cost and he shall ensure that his employees regularly use such safety gears while executing COMPANY's work.

    - The CONTRACTOR shall be responsible for discipline of his manpower and shall adhere to the disciplinary procedure set by the COMPANY at site. The COMPANY shall be a t liberty to object to the presence of any representative or employees of the CONTRACTOR at the site, if in the opinion of the COMPANY such manpower has done any act of misconduct or negligence or otherwise undesirable, then the CONTRACTOR shall remove such a person objected to and provide a competent replacement immediately.

    - The CONTRACTOR shall ensure that he has complied with the following: -has paid minimum wages to his manpower as per the rate notified from time to time by the Government of Telangana. Contractor shall disburse the salary of his staff through ECS only. No payment by cheque / cash is acceptable.

    - Deduct and deposited ESI and PF contribution. Copies of the same shall be submitted.

    - The COMPANY reserves the right to demand the CONTRACTOR's services on holidays as well as beyond the normal working hours.

    - The CONTRACTOR will ensure that none of their person is engaged in any unlawful activities subversive of the COMPANY's interest failing which suitable action may be taken against the CONTRACTOR as per the terms and conditions of this tender.

    - The CONTRACTOR shall be liable for payment of all taxes and duties as applicable, to the State/ Central Govt. or any local authority.

    - The CONTRACTOR's employees shall not be treated as COMPANY's employees / persons for any purpose whatsoever & facilities/ benefits applicable to the COMPANY's employees shall not be applicable to CONTRACTOR's employees. If due to any reasons whatsoever the COMPANY is made liable to meet any obligation under any of the laws & enactment etc, for any reason whatsoever the same shall be recovered from the CONTRACTOR or from any of the bills payable to him or failing which it shall be recovered as per law.

    - The CONTRACTOR shall be responsible and shall comply with the provision of all the STATUTORY ACTS APPLICABLE. Special attention of the CONTRACTOR is drawn towards the compliance of provision of the following statutes: (along with the latest amendments/additions):

    - The Child Labour (Prohibition and Regulation) Act, 1986.

    - The Contract Labour (Regulation and Abolition) Act, 1970.

    - The Employee's Pension Scheme, 1995

    - The Employee's Provident Funds and miscellaneous provisions Act, 1952.

    - The Employees State Insurance Act, 1948.

    - The Industrial Disputes Act, 1947.

    - The Maternity Benefit Act 1961.

    - The Minimum Wages Act, 1948.

    - The Payment of Bonus Act, 1965.

    - The Payment of Gratuity Act, 1972.

    - The payment of Wages Act, 1936.

    - The Telangana Shops & Establishment Act, 1988.

    - The Workmen's Compensation Act. 1923.

    - The Employer's Liability Act, 1938.

  - Subletting of Work Order:

The Contractor shall not sublet, transfer, assign Work or any part thereof without the written permission of the Company.

  - RISK AND COST:

The company at his option will be entitled to terminate the Contractor and to carry out work from elsewhere at the risk and cost of the Contractor either the whole or any part which the Contractor has failed to perform, the best and the nearest available substitute there from the Contractor shall be liable for any loss which the Company may sustain by reason of such risk purchases.

##### SECTION – 2 : FINANCIAL

    - Prices:

- Firm Prices: The prices quoted shall be FIRM and without any Price Variation except for copper, should be exclusive of all taxes.

- Any variation or upward or down ward revision in the GST and other legally possible duties and levies will be borne by TGSPDCL.

- Even though composite firm price is quoted, breakup for all duties, taxes, freight, insurance, etc., shall be furnished.

2.1.4     Price Variation:

- For Copper winding wires in respect of item number- (2) Providing of  new insulated   copper winding in place of Damaged windings (HV and LV) for material portion only of the price schedule, Price variation will be considered on the following basis, if the Copper winding wire required for carrying out repairs to PTRs are not supplied by TGSPDCL.

- Hike in the base price of the raw materials (Copper) for drawing out winding wire as per the rates published in IEEMA Journal will be considered for variation upward or downward to the rates quoted and accepted for Copper coils.

- The base price of Copper [Price of copper wire rod of previous month] published in IEEMA Circular Code Nos. IEEMA(PVC)/PWR_DIST_TRF as on the first working day of the month, one month prior to the date of Bid opening. In this instant, the base price shall be the price of Copper as on 01.07.2024 and applicable base price is Rs. 849.090 per Kg. The final price of Copper will be the price prevailing as on the 1st working day of the month, one month prior to the date of delivery of the repaired PTR.

- The price variation is applicable for the repaired PTR subject to the following conditions:

- The Price variation clause will be applicable to the repaired/ overhauled PTRs for which the winding wire is supplied by     the contractor.

- The Price variation is applicable for the Copper coils only.

- The Positive price variation is applicable for the sick PTR which is repaired/ overhauled and handed over within 60 days for PTRs of capacity upto 8 MVA and 90 days for PTRs of capacity above 8 MVA and as per the Delivery clause of the Bid Specification only.

- Negative price variation is applicable for all the sick PTRs repaired/ overhauled, irrespective of date of delivery.

- In case of upward trend, the price variation will be limited to maximum of 30% over the base price.

- There is no ceiling limit and no conditions on negative price variation.

- Applicability of price variation will be based on quoted/confirmed percentage rate.

- The Repairer/Contractor shall submit an undertaking with his bills that there is no downward variation in the price of copper with reference to base price. If there is downward variation the Repairer/Contractor allows suitable reduction on the price, subject to final adjustment.

- In case of upward variation of prices separate bills for price variation shall be claimed which shall be arranged after verification of the relevant "IEEMA journals”.

  - Currency of Payments:

  - All payments will be made in non convertible Indian Rupees.

  - All royalties for patents or charges for the use or infringement thereof that may be involved in the construction or use of any equipment shall be included in the tender prices. The tenderer shall protect the TGSPDCL against any and all such claims arising on account of the use thereof.

- Performance Security:

- The successful Bidder to whom the contract is awarded will be required to furnish the performance security of 5% of the value of the contract for proper execution of the contract, and valid for a period of 1 and half year (18 months) over and above the specified completion period. The performance security will be furnished by way of DD/Bank Guarantee in the prescribed format.

- If the bidder fails to furnish the performance security as specified within fifteen days of the award of contract is liable for cancellation of the contract and forfeiture of the Bid security.

  - Terms of Payment:

The following terms of payment are only acceptable. Tenders received stipulating terms other than the following terms will be invalidated.

    - Payment for the repair/overhaul work to power transformer will be made up to 90% of the contract work at the rates approved in the schedules for the items of works done. For this purpose the successful tenderer (s) shall submit bills with full details of the work done on each unit of transformer on completion of repair/overhaul, to the concerned Divisional Engineer to ensure payments in time. The balance 10% will be paid after completion of one and half year (18 months) performance guarantee reckoned from the date of commissioning as specified or after all the removed components of the sick transformers are handed over to the TGSPDCL whichever is later. In case 100% payment is required, the repairer has to furnish Performance Security Bank Guarantee for 5% of the contract value. This is in addition to the 5% Performance Security Bank Guarantee to be furnished against clause No.2.3.1.

    - No interest will be payable in case the payment is delayed for whatsoever reason.

    - The Repairer should invariably submit test certificates as soon as inspection is completed so that the test certificate can be examined and approved for issue of dispatch instructions.

    - If the Contractor/Repairer has received any over payments by mistake or if any amounts is due to the TGSPDCL due to any reason, when it is not possible to recover such amounts under the contract resulting out of this specification, the TGSPDCL reserves the right to collect the same from any other amounts and/or Bank Guarantees given by the Contractor/Repairer due to or with the TGSPDCL.

    - When the Repairer does not at anytime, fulfill his obligations in replacing/ rectifying, etc., of the damaged/defective materials in part or whole promptly, TGSPDCL reserves the right not to accept the bills.

    - The repairer shall not claim any additional amount for the items other than mentioned in the Price Schedule that are required for completing the work in totality.

- Responsibility of Tenderer for Loss or Damage:

    - Tenderer is responsible for the safe custody during the repairs and delivery of the repaired/overhauled Power Transformer in good condition at the destination. . He should acquaint himself of the conditions obtaining for handling and transport of Power Transformers and shall include and provide for security and protective packing of Power Transformers so as to avoid damage in transit.

    - External damages or shortages that are prima-facie the results of rough handling in transit or due to defective packing will be intimated within a fortnight of the receipt of the equipment/materials. Internal defects, damages or shortages of any integral parts which cannot ordinarily be detected on a superficial visual examination though due to bad handling in transit or defective packing will be intimated within 2 months from the date of receipt of the equipment/materials. In either case the defective or damaged equipment/materials should be replaced by the contractor/repairer at free of cost to the TGSPDCL. If no steps are taken within 15 days of receipt of intimation of defects or such other reasonable time as the TGSPDCL may deem proper to afford, the TGSPDCL may without prejudice to its other rights and remedies cause to be repaired or rectified the defective material or replace the same and recover the expenditure incurred therefore from the deposit such as Earnest Money, Security and Performance or other amounts available with TGSPDCL or by resorting to legal action.

    - In the event of the goods and materials handed over to the Contractor/Repairer for execution of this contract being lost, damaged or destroyed while being in the custody of the Contractor/Repairer before being taken over by the TGSPDCL the contractor shall be liable to make good the loss without any extra charges to the TGSPDCL.

    - To provide the security for the TGSPDCL equipment under custody of the successful tenderer (s), the tenderer shall provide Bank Guarantee /Insurance for the value of equipment under his custody as intimated by the Superintending Engineer/Operation\ SCADA concerned. Indemnity Bond against Bank Guarantee towards value of the equipment under custody is not acceptable. The Acquisition Value should be taken as the Original Cost of the Asset along with the Book Value from the Asset Balances in SAP. Where SAP value of Power Transformer is not available the value (E) is arrived as follows.

E = Book value of the equipment x (1-0.0784 x n)

Where 'n' is years of service of equipment subject to a maximum of 25 years.

  - Delay Beyond Contractor’s/Repairer’s Control:

    - The contractor shall not be entitled to claim compensation on account of delays or hindrances to the works for any cause whatsoever nor the Contractor/Repairer shall be entitled to extension of time except in case of force majeure. Should the cause of delay or hindrance be on account of force majeure conditions, the reasons attributable to the TGSPDCL the Superintending Engineer/Operation/SCADA  will consider whether it is possible or not to grant an extension of time to compensate for this delay or hindrance. The Contractor/Repairer will not, however, be eligible for any compensation by way of increase in the rates for the works executed beyond the contract period.

    - Extension of the Time for Completion:

    - When a work cannot be completed within the completion period indicated for reasons beyond the control of the Contractor/Repairer, extension of time shall be granted only on the issue of an undertaking by the Contractor/Repairer that he will not put forth at a later date, claims for extra payments towards increased overheads, labour costs, etc.

  - Force Majeure:

- Force majeure is herein defined as any cause which is beyond the control of the Contractor/Repairer or the TGSPDCL, as the case may be, which they could not foresee or with a reasonable amount of diligence could not have been foreseen and which substantially affect the performance of the contract, such as :

- Acts of God, natural calamities, including but not limited to floods, droughts, earthquakes and epidemics;

- Acts of any Government, domestic foreign, including but not limited to war, declared or undeclared priorities, quarantines, embargoes;

- Acts of public enemy, accidents and disruptions including but not limited to fires, explosions, breakdowns of essential machinery or equipment.

- Transportation delay due to force majeure accidents.

- Strikes lockouts and sabotages;

- Riots and civil commotions;

Provided that the successful Tenderer/Repairer shall within fifteen (15) days from the occurrence of such a cause notify TGSPDCL in writing of such causes.

- Progress of Work:

  - If it is found that the progress of work is not commensurate with the programme of completion, TGSPDCL will be entitled to terminate the contract in part or full giving 15 days notice and get the balance works completed through other agencies at the contractors cost and risk.

- Cost Towards Empty Oil Barrels:

  - If the empty oil barrels are not returned back/devoluted, the cost of the empty oil barrels will be charged as per the latest auction rate of TGSPDCL, prevailing on the date of approval of estimate for repair/overhaul of the Power Transformer and taxes as applicable will be charged.

- Shortage of Oil Recovery Cost:

  - The new transformer oil will be allotted to the repairer with 1% extra quantity of oil towards handling and filtration losses. If transformer oil found short after transporting the repaired/overhauled Power Transformer with oil to the allotted substation then the cost of the oil at the latest procurement rate of new transformer oil by TGSPDCL shall be recovered from the bills of the repairer.

- Cost towards the damaged parts:

  - All the damaged parts including the damaged HV/LV winding coils (Copper scrap) shall be handed over back to TGSPDCL along with the repaired/overhauled Power Transformer. The Copper winding coils removed from the repaired Power Transformer shall be burnt/cleaned before handing over and reduction in weight due to removal of insulation is allowable upto 12%. This quantity should match with the replaced quantity. The amounts of short fall in quantity if any, of damaged parts shall be recovered from the bills of the repairer @ latest auction rates of TGSPDCL and for winding coils at the ‘Copper Scrap’ rate at ‘Mumbai Market’ published in the ‘The Economic Times’ plus applicable taxes if any. All damaged windings along with other insulating material shall be cut into small pieces and destroyed in presence of Engineer in charged at the time of Joint Inspection Report. Repairer has to take the photographs of above destroyed scrap windings & should be handed over to the engineer in charge.

- Transportation of Power Transformers:

  - TGSPDCL reserves right to take up the work of Transportation of Power Transformers and other equipment of Power Transformers by departmentally. Entrusting the work of Transportation of Power Transformers to the Repairer or to take up the work by departmentally shall be at the discretion of the concerned Superintending Engineer/ Operation/SCADA circle depending on the availability of departmental trailers/lorries and other criteria of urgency and cost economics of the prevailing conditions.

  - The offered/accepted rate for transport of Power Transformer i.e., per MT/km and other equipment of Power Transformer is assumed on the prevailing rate of diesel on the date of bid submission. The same rate is applicable if diesel cost is decreased/ increased by 10%. The decrease/increase in transport cost will be considered only on the less/excess % beyond 10% and rate payable will be decreased/ increased only to the extent of the % decrease/ increase in the diesel cost beyond 10%. For this purpose the prevailing rate of diesel cost at Hyderabad or Secunderabad will be considered.

  - Repairer shed shall be within boundary of TGSPDCL.

2.14   Loading /unloading of Power transformers:

Loading /unloading of Power transformers failed under BGP will be arranged departmentally at sites of TGSPDCL.

In case of Power Transformers failed under Repair Guarantee Period (RGP), the loading / unloading of PTRs at TGSPDCL sites shall be carried out by the repair agencies at free of cost. If the loading/unloading of RGP power transformers is arranged departmentally, the expenditure incurred towards the same will be deducted from the bills of the repairer.

SECTION – 3 : TECHNICAL

  - Scope:

    - This specification provides for repairing/overhauling of 33/11 kV sick power transformers including transportation to tenderers repair works from site of the TGSPDCL, arranging joint inspection, estimation of repairs, carrying out repairs/overhaul, testing and re-transporting of repaired transformer to the allotted substations/stores anywhere in the jurisdiction of TGSPDCL including loading and unloading. The period of proposed contract will be for two years with a provision to extend the time period with same terms and conditions.

    - The particulars of rating and general data in respect of sick power transformers covered for repair/overhauling by this specification are as given below:

| Sl.No. | Particulars |  | Rating and General Data |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| i) | Particulars of the Specification |  | IS 2026/1981 (as on date of mfg.) |  |  |  |
| ii) | Type of Transformer |  | Separate winding transformer |  |  |  |
| iii) | No. of phase and frequency |  | Three phase, 50 Hz. |  |  |  |
| iv) | Type of cooling |  | ONAN |  |  |  |
| v) | Rated voltage HV/LV |  | 33,000/11,000 volts |  |  |  |
| vii) | Rated capacity (MVA) |  | 3.15, 5.0, 7.5/8.0&12.5/15/16 |  |  |  |
| viii) | Impedance voltage losses |  | As provided in the sick unit |  |  |  |
| ix) | Tapping and Tap changer requires |  | As provided in the sick unit |  |  |  |
| x) | Highest voltage of equipment |  | (HV/MV) 36000/12000 volts |  |  |  |
| xi) | Method of system earthing |  | All neutral bushings earthed |  |  |  |
| xii) | Connection Symbol |  | As provided in sick unit |  |  |  |
| xiii) | Special requirement of transport. |  |  |  |  |  |
|  | a) | Approx. Max. Weights | 10 MT | 12 MT | 20 MT | 25 MT |
|  | b) | Approx. Max. Qty Oil | 3 KL | 4 KL | 5 KL | 6 KL |
|  | c) | Approx. Max. dimensions (l x b x h in metres) | # 5x4x3.5 | 5x4x4 | 6x4x4 | 6x5x4 |

  - Compliance with Specifications:

3.2.1 	Except where otherwise specified or implied herein the power transformers shall comply with latest publication of Indian Standards 2026/1977 (hereinafter referred to I.S.)

    - Losses and impedance voltage and connection symbol of each transformer shall be as per the original design values. The tolerance for these values of repaired/overhauled Power Transformer shall be as per IS 2026.

  - Design and Standardization:

    - All materials used shall be of the best quality and class and shall be most suitable   for satisfactory working under the conditions specified and shall withstand the variation of the temperature and atmosphere conditions. There should not be any deterioration or distortion in the materials under load conditions, which may set in undue stresses. The repairs/overhaul to sick Power Transformers should be carried out with latest methodologies by adopting modern techniques.

    - All connection and contacts shall have adequate cross-section and surface area for carrying continuously the specified currents without over heating and fixed connections shall be carried/secured by bolts and nuts or set of screws of ample size, adequately locked and locking units shall be provided for stud connections. All leads from the winding to the terminals and bushings shall be rigidly supported to prevent damages due to vibrations/transportation. It would be preferable to use sleeves wherever applicable. All current carrying joints in the windings and the leads shall be welded or rigidly clamped.

    - Transformer losses and impedance voltage on repaired transformer shall be as per original design values. The tolerances for these values on repair units shall be as per IS:2026. Vector group shall be maintained as per original transformer.

    - The clearances in air between live conductive parts and live conductive part to earthed structures (in air) shall be as indicated below:

| Nominal Voltage | System kV RMS | Test Voltage Impulse kVP | Clearance |  |
| --- | --- | --- | --- | --- |
|  |  |  | Phase to Phase (mm) | Phase to Earth (mm) |
| 33 kV | 36 | 170 | 350 | 320 |
| 11 kV |  | 75 | 280 | 205 |

  - General:

    - The materials such as winding coils, transformer oil, etc., handed over to the successful tenderer for repair work should be accounted for and removed parts of sick power transformer such as windings, discarded transformer oil, core, etc., should be handed over back to the TGSPDCL along with the repaired units to Divisional Engineer or authorized representative in charge of the repairs work.

    - All the insulating materials required are to be provided by the successful tenderer as per the specification.

    - Departmental labour will not be spared for the execution of the work by the successful tenderer.

  - Bolts & Nuts:

3.5.1 	Steel Bolts and nuts exposed to atmosphere with suitable finish like cadmium plated or Zinc plated passivity shall be used for diameters above 6 mm.

3.5.2	All nuts, bolts shall be invariably provided with suitable size of spring washers and adequately tightened. Any pins and internal bolts shall be locked, with the exception of those external to the transformer.

3.5.3	On outdoor equipment, all bolts, nuts and washers in contact with non-ferrous parts, which carry current, shall be of phosphorous bronze, where the transfer of current is through the bolts.

3.5.4	If bolts and nuts are placed so that they are inaccessible by means of ordinary spanners, the tenderer shall provide suitable special spanners. Insulation core bolts shall be thoroughly inspected and if required new insulation bolts shall be provided for top yoke and bottom yoke.

  - Core:

    - The core of the sick power transformer shall be thoroughly examined at the time of joint inspection and the repairer shall do compulsorily core building after thorough cleaning and inspection of each and every lamination of all the legs and further the parts of damaged core shall be reconstructed from high-grade cold rolled, non-ageing grain oriented. (C.R.G.O.), Silicon steel laminations of M4 or MOH Grade.

    - The magnetic circuit i.e., core, yoke, clamping structure shall be thoroughly checked and if found abnormal, remedial steps shall be taken.

    - All core bolts shall be reinsulated with Hylum pipe of suitable diameter. If clamping arrangement is possible the same shall be taken adhering to all precautions. Locking of core clamping bolts shall be done. The insulation core bolts shall be thoroughly inspected and if required new insulation bolts shall be provided for top yoke and bottom yoke.

    - The repairer shall make the clamping arrangement for core and winding such that they shall not be disturbed while transport, installation or in service. In case there is no provision of the rods in the clamping arrangements for the same shall be provided in repaired transformers without any additional charges.

    - Earthing of core clamping structures: The top core clamping structure and clamping structure shall be earthed by adopting standard method as per the manufacturing practices and CBIP specification.

  - Windings:

    - HV/LV winding coils that have failed shall be repaired by utilizing coils made up of suitable new insulated wires/strip of equivalent current carrying capacity.  All other HV/LV winding coils insulation, which is suspected to have weakened, shall be reinsulated after removing the old insulation, straightening and polishing the conductor.  All inter layer insulation, insulation between core and LV windings, between HV and LV windings shall be replaced with new insulating materials procured from reputed firms having ISI certification mark.  The phase barriers if provided in original design shall also be replaced with similar insulation boards/barriers of standard make (Raman or Senapathy).

    - Windings replaced or re-insulated shall be fully insulated as defined in ISS 2026.  All neutral points shall be insulated for full voltages as specified in ISS 2026.

    - The insulation of the transformer winding shall be of high quality and resistant to insulating composition liable to soften, loose out, shrink or collapse during service.

    - Coil clamping arrangements and finished dimension of all oil ducts shall be such as it will not impede free circulation of oil within the ducts.

    - The Insulation Paper used for winding shall be as per IS9335/IEC. Thickness and Tolerance as per IEC 60554 standard of any TSTRANSCO approved make. The contractor shall at the time of inspection produce a certificate from the manufacturer that the Insulation paper conform to the latest IS9335/IEC and IEC 60554 standard.

  - Tank, cooling plant, cleaning and painting:

    - The transformer tank and other accessories shall be thoroughly inspected for any leakages, cracks, blow holes, etc., before painting and any defects noticed shall be rectified by approved methods, and any deformities in tank shape and other accessories are to be corrected before painting.

    - The associated pipe work i.e. main tank oil feed pipe, conservator drain pipe, pressure equalizer pipe, breather extension pipe, explosion vent pipe and any other pipes shall be thoroughly cleaned and the welding joints shall be thoroughly checked by passing hot oil at 100o C. If any leakage is observed, remedial action shall be taken.

    - All the radiators shall be thoroughly cleaned with hot oil. All the welding joints shall be checked for any leakage and rectification shall be done. Teflon washers for air release plugs shall be replaced. Anti-vibration stiffeners shall be provided.

    - Cleaning and painting: All internal and external structural steel works shall be cleaned of all scale and rust by shot blasting or by other approved methods. All non-galvanized parts shall be thoroughly cleaned and phosphorous treatment shall be given. The transformers including radiators OLTC and other surfaces shall then be applied with two coats of primer if necessary before finally spray painted with Siemens Grey OF RIL 7032 or 631 and shall comply with ISS 5. The Paint shall be preferably with Epoxy base and should be non-fading quality.

    - Gaskets:

    - All gaskets used for making oil tight joints shall be of proven material and qualities such as granulated core bonded with synthetic rubber or synthetic rubber gasket.

    - The Gaskets shall be replaced with RC70C only.

    - The gasket sets shall be type (B) conforming to IS-4253/P-II/1980 and any amendment thereof. The gasket to be used in the repair of these transformers shall be of TSTRANSCO approved make. The contractor shall at the time of inspection produce a certificate from the manufacturer that the gasket conforms to the latest ISS-4253/Part-II.

3.10	Protective accessories:

    - Pressure relief device: The diaphragm used for pressure release devices shall operate at a static pressure of less than hydraulic test pressure for transformer tank.

    - Pressure release valve: The pressure release device shall be of heavy duty and shall be capable of actuating a limit switch of 2 NO contacts. One NO shall be wired to the trip circuit and other to the alarm circuit in the marshalling box.

    - Bucholtz relay:  The Gas operated relay shall comply with IS 3637. Relay with two floats shall be provided to the main tank and single float to the OLTC. One contact of main Bucholtz relay is wired for trip circuit and other to the alarm circuit.

    - Oil/Winding temperature meters: Oil and winding temperature meters shall be heavy-duty mercury type with 3m capillary. The meter shall have invariably two potential free NO mercury contacts.

    - Silica Gel breathers to be provided shall be of Al. metallic body. All the other fittings and accessories shall comply with IS 3639

  - Transformer Oil:

    - New transformer oil used in the repaired unit shall be as per specification in the ISS 335 and it shall be free from moisture and have uniform quality throughout.

    - In case new oil is to be topped up through filter after obtaining required I.R. values, handling and filtration losses up to maximum of 1% is permissible.

  - Bushings:

    - Bushings replaced to the power transformer shall conform to IS 3347 and IS 2026 for electrical characteristics, materials and dimension.

    - The bushings for 33 kV shall be of 36 kV, 600 A with detachable stem (3/4”) and for 11 kV shall be of 12 kV LV Bushing, 630 A with detachable stem (3/4”)

    - All necessary modifications for fixing the bushings and any other accessories on the main tank and on the transformer shall be done by the repairer.

  - OLTC

    - All the moving contacts and fixed contacts including the copper tubes and assembly shall be thoroughly cleaned with CTC/CFC.

    - All barrier board connections from OLTC side shall be cleaned thoroughly and all the connecting links shall be tightened.

    - All the gaskets shall be replaced with RC70C synthetic rubber bonded cork gaskets.

    - In the event of replacing the moving and fixed contacts the locking pins, circlips shall be new one only. The old locking pins shall never be used.

    - The Sludge in the OLTC tank including the tapping switch shall be thoroughly cleaned with hot oil and all traces of carbon shall be removed.

    - The healthiness of transition resistors, Motor driving mechanism, Energy accumulator, clutch bearing mechanism, Geneva wheel roller bearing shall be thoroughly checked and minor repairs shall be carried out.

    - The Cam faces, gear teeth, rollers, and wiping surfaces are to be lubricated with molybdenum disulphide in a lithium grease base.

    - All mechanical operations and electrical operations shall be checked including the TPI.

    - All the mechanical and electrical interlocks including the isolation of electrical drive system in the event of mechanical operation of the OLTC shall be checked thoroughly and parts like resistances of the TPI, bolts and washers, locknuts except contact points and terminal barrier board inclusive of OLTC both in mechanical and electrical modes shall be thoroughly (manual) checked at the repair shop before dispatch.

  - Tests:

    - The following routine acceptance tests shall compulsorily be conducted on the repaired transformers at work spot in the presence of TGSPDCL representative and record of the same made available. The test values shall be guaranteed as per IS: 2026.

- Measurement of winding resistance.

- Measurement of voltage ratio, polarity and phase relationship.

- Measurement of impedance voltage & load loss.

- Measurement of no load losses, no load current and unbalance currents (neutral current 2 to 8% of measured value.

- Measurement of insulation resistance (Refer clause 17-9 of ISS 2010)

- Induced over voltage withstand test.

- Separate source voltage withstand test.

- No-load loss at 100%

- % Impedance ( negative tolerance will not be allowed )

- Regulation at UPF.

- Regulation at 0.8 PF

- Tests on OLTC, wherever appropriate

- Tests on Oil (as per ISS-335) in case oil is either re-conditioned or replaced with new oil by repairer.( BDV, Acidity and water ppm)

- Magnetic balance test for V&I

- Oil pressure test

- Tan delta test of winding. ( tan delta with capacitance)

- Frequency response analysis ( SFRA)

- Furan Test.

    - Any other tests, deemed necessary by TGSPDCL shall also be conducted as mentioned in the joint inspection report.

    - The test shall be carried out as per ISS 2026 and approved/CBIP, test standards.  The test values shall be guaranteed against ISS 2026.

    - The voltage withstand values for tests (viz., Induced over voltage withstand test and Separate source voltage withstand test) shall be 0.75 times of the specified values (full test values) as per IS 2026.

    - The IR values between windings and between windings to earth should be checked. While checking IR values no external connection lines, lightning arresters, etc., shall in service. Bushings shall be thoroughly cleaned before taking IR values. A motorized 5000 V Megger should be used for measuring IR values. Every time the voltage shall be applied for 1 minute.

    - The assembled core and windings shall be dried in suitable heating chamber till the proper megger value is received. The minimum insulation values shall be as detailed below. Though the values are indicative the drying out process shall never be stopped till steady values are recorded.

| IR values | @ 30o C | @ 40oC | @ 50o C | @ 60o C |
| --- | --- | --- | --- | --- |
| 33 kV to earth | 500 | 250 | 125 | 65 |
| 11 kV to earth (Mega-ohms) | 400 | 200 | 100 | 50 |

If any damage caused during handling, any utilization of inferior raw material, bad workmanship, improper and abnormal operation, careless drying out, the repairer shall be held responsible and consequential damage shall be done free of cost and the decision of TGSPDCL in this regard is final.

    - After completing all the tests, the transformers should be transported and handed over to the departmental engineer in charge of the work at respective substations

  - Additional Name Plate:

  - Immediately after completion of repairs/overhaul and test, the repairer shall affix on the transformers at free of cost, just below the manufacturers name plate (metallic) of suitable size with the following details engraved  on it:

  - Name of the repairer

  - Repaired/overhauled tested on:

  - Delivered on:

  - Repair Guarantee Period valid upto:

  - Voltage Conversion or Uprating/Derating of Power Transformers:

  - In case the power transformers ratings is enhanced or derated from the original rating, the rates accepted by this tender will be applicable for the items of works covered for such works.

# BID FORM

Specification No.:	CE /O&M -01/2024-25

Name of work:	Repairing/overhauling of sick 33/11 kV Power Transformers of different makes and various capacities available at various substations and sites of TGSPDCL

Date: ………

To

The Chief Engineer /O&M,

TGSPDCL, Corporate Office

6-1-50, 5th Floor, A-Block,

Mint Compound,

Hyderabad 500 063.

Dear Sir,

Having examined the tender specification, together with the accompanying General conditions therein referred to, we the undersigned hereby offer to provide and carry out the work of Repairing/Overhauling of sick 33/11 kV Power Transformers of different makes and various capacities available at various substations and sites of TGSPDCL according to the said specification, general conditions at the rate mentioned in the schedule of prices/at the discount offered.

We undertake, if our Bid is accepted, to complete the repair/overhaul work of sick Power Transformer within the delivery time specified in the schedule. We hereby guarantee the particulars entered in the schedules attached to the tender. We will obtain the guarantee of a bank in a sum equivalent to 5% of the Contract Price for the due performance of the Contract, in the form prescribed by the TGSPDCL.

In accordance with the clauses of this specification, we confirm that having enclosed the securities as mentioned in the summary sheet i.e., the Bid Security/Earnest Money Deposit (EMD).

We hereby agree for the standard payment terms of TGSPDCL.

We agree to abide by this Bid upto 90 days (for the Bid validity period) specified in Clause and it will remain binding upon us and may be accepted at any time before the expiry of that period.

Until a formal contract is prepared and executed, this Bid, together with your written acceptance thereof and your notification of award will, constitute a binding contract between us.

We understand that you are not bound to accept the lowest or any bid you may receive.

We certify/confirm that we comply with the eligibility requirements as per clause of the tender specification.

Signature:

Designation with Seal

BID SECURITY FORM

To

The Chief Engineer/O&M

Corporate office ,TGSPDCL

Whereas.  .............. (hereinafter called "the Bidder") has submitted its Bid dated (date of submission of bid) for the supply of.  ....................(name and /or description of the Materials / equipment) (hereinafter called "the Bid").

KNOW ALL PEOPLE by these presents that WE.  .............(name of bank) having our registered office at.  ...........(address of bank)(hereinafter called "the Bank"), are bound unto.  ...............(name of Purchaser) (hereinafter called "the Purchaser") in the sum of                   for which payment well and truly to be made to the said Purchaser, the Bank binds itself, its successors, and assigns by these presents. Sealed with the Common Seal of the said Bank this          day of             2024 .

THE CONDITIONS of this obligation are:

1.	If the Bidder

a) 	withdraws its Bid during the period of bid validity specified by the Bidder on the Bid Form; or

- does not accept the correction of errors in accordance with the Bid Specification, or

2.	If the Bidder, having been notified of the acceptance of its bid by the Purchaser during the period of bid validity;

(a)	fails or refuses to furnish the performance security, in accordance with the Bid Specification.

(b)	fails or refuses to execute the Contract Form if required; or

We undertake to pay the Purchaser up to the above amount upon receipt of its first written demand, without the Purchaser having to substantiate its demand, provided that in its demand the Purchaser will note that the amount claimed by it is due to it, owing to the occurrence of one or both of the two conditions, specifying the occurred condition or conditions.

This guarantee will remain in force up to and including forty five (45) days after …………….(Specification Date) the period of the bid validity i.e., total for 135 days from the date of bid opening, and any demand in respect thereof should reach the Bank not later than the above date.

.  ....................

(Signature of the Bank)

NOTE:	This will be executed on a Rs.100/- non-judicial stamp paper issued by a Nationalized/Scheduled Bank.

PERFORMANCE SECURITY FORM

(10% of the order/repair value of Power Transformer)

To

The Superintending Engineer,

Operation/SCADA circle,

……………………………...,

……………………………….

## WHEREAS ………………………………………….. (Name of repairer) (hereinafter called “the repairer/contractor”) has undertaken, in pursuance of Contract No. ……….. dated ……………… 2024 to Repair/Overhaul of sick 33/11 KV Power Transformer of ………MVA. ………..make and bearing Sl.No. ………… failed/released at ……………..  substation of ………………. circle of TGSPDCL  (hereinafter called “the Contract”).

AND WHEREAS it has been stipulated by you in the said Contract that the Repairer/Contractor will furnish you with a Bank Guarantee by a recognized Bank for the sum specified therein as security for compliance with the Repairer’s/Contractor’s performance obligations in accordance with the Contract.

AND WHEREAS we have agreed to give the Repairer/Contractor a Guarantee:

THEREFORE WE hereby affirm that we are Guarantors and responsible to you, on behalf of the Repairer/Contractor, upto a total of …………….. (Amount of the Guarantee in words and figures) and we undertake to pay you, upon your first written demand declaring the Repairer/Contractor to be in default under the Contract and without cavil or argument, any sum or sums within the limit of ……… (Amount of Guarantee) as aforesaid, without your needing to prove or to show grounds or reasons for your demand or the sum specified therein.

This guarantee is valid until the ... day of.....2024.

Signature and Seal of Guarantors

………………………………….

Date ……………………... 2024.

…………………………………..

…………………………………..

Address: ………………………...

…………………………………..

…………………………………..

NOTE:	This will be executed on a Rs.100/- non-judicial stamp paper issued by a scheduled Bank.

## SCHEDULE – A

PARTICULARS OF TENDERER

1.	Name, full Address,

Telephonic Address and Phone No.

Email address

2.	Nature of tenderer’s organization please state whether

- Individual

- Registered partnership firm

- Unregistered partnership firm

- Private Limited Company

- Public Limited Company

- Others (Please specify)

- Does your firm come under the scope of the

Industries Act and if so number and date of registration

Or license particulars and type of industry.

Type of Industry

- Class A, B, etc.

- Large, Medium or SSI

- List and full address of Partners in case of

partnership firm)/Directors (in case of Limited Company)

5.	List of repair, testing centers with full address

6.	Sales tax Registration

7. 	Have you obtained Income Tax clearance for

- Applicant firm

- Proprietor

- Individual Partners.

8.	List of Authorized persons to represent the company

for signing contract documents etc.

9.	Nature of business of tenderer enclosures required.

- Memorandum of Tenderers firm

- Articles of Association

- Certificate of Incorporation

- Entry in form ‘A’ from Registrar of firms

- Income tax clearance certificate.

- Last annual report.

- Profit and loss account and balance sheet.

- Auditors statement indicating the results

Of operation and financial position of the firm.

- Power of attorney and copies of membership documents.

- Power of attorney for authorized persons of the tenderer to

Sign contract documents.

### SIGNATURE OF THE TENDERER

Note:  This form shall be signed by the person/persons competent as detailed below.

a) Proprietor ship firm		:	Sole proprietor of the firm

b) Partnership firm	:	All partners or by any of the partners who holds general power of attorney authorizing him to sign for and on behalf of the firm in contractual obligations (Power of attorney with certified copy thereof  to be enclosed.

c) Companies	:	By Managing Director or any one of Directors if there is no Managing Director. Any person who holds general power attorney in his favour from the firm giving him authority to do so (Power of attorney with certified copy thereof to be enclosed).

##### SCHEDULE – B

BANK ACCOUNT DETAILS FOR REAL TIME GROSS SETTLEMENT

- Name of the Bank		:

- Name of the Branch		:

- Branch Code			:

- MICR Code			:

- IFSC Code			:

- City				:

- Account Number		:

- Income Tax PAN Number	:

- GST  Registration Number	:

- Place of  GST Registration	:

- Date of  GST Registration	:

### SIGNATURE OF THE TENDERER

Note:	The tenderer should furnish copies of all relevant registration certificates

##### SCHEDULE – C

DETAILS OF TECHNICAL PERSONNEL IN THE ORGANIZATION OF THE TENDERER

(Pertaining to Power Transformer Repairs/Overhauls)

Name of the Tenderer:

| Sl. No. | Name | Qualification experience and details carried out. | Professional experience and details of works carried out | Field in which now engaged | Remarks |
| --- | --- | --- | --- | --- | --- |
| A) | Design Engineer |  |  |  |  |
| 1 |  |  |  |  |  |
| 2 |  |  |  |  |  |
| B) | Production Engineer |  |  |  |  |
| 1 |  |  |  |  |  |
| 2 |  |  |  |  |  |
| C) | Supervisory Staff |  |  |  |  |
| 1 |  |  |  |  |  |
| 2 |  |  |  |  |  |
| D) | Skilled Workers |  |  |  |  |
| 1 |  |  |  |  |  |
| 2 |  |  |  |  |  |
| 3 |  |  |  |  |  |
| 4 |  |  |  |  |  |
| 5 |  |  |  |  |  |

Note:	The tenderer should not employ any retired TGSPDCL/DISCOM Official under him within a period of two years from the date of his retirement from service without obtaining prior permission from DISCOM/Government.

### SIGNATURE OF THE TENDERER

SCHEDULE - D

DETAILS REGARDING FINANCIAL STANDING OF THE BIDDER

(Certificates from the bankers in proof of cash balance and other credit facilities shall be furnished in support of the above information without fail.)

The following particulars may be filled in.

| Sl. No. | Name of the Bank | Actual balance at the credit of the tenderer | Permissible overdraft | Total credit | Remarks |
| --- | --- | --- | --- | --- | --- |

### SIGNATURE OF THE TENDERER

SCHEDULE - E

DETAILS OF FINANCIAL TURNOVER

(Pertaining to Power Transformer Repairs/Overhauls)

Name of the Tenderer:

| Sl. No. | Name of the Work done | Value of the each work corresponding to turnover |
| --- | --- | --- |

Note:	The tenderer shall furnish the Latest Income Tax Return & Turn over certificate certified by Chartered Accountant.

### SIGNATURE OF THE TENDERER

SCHEDULE - F

DETAILS OF MACHINERY, EQUIPMENT AVAILABLE AT

REPAIR CENTRE (CRITICAL EQUIPMENT)

Name of the Tenderer:

Location/Place:

| Sl. No. | Description of the machinery/equipment | Capacity of the machine/equipment | Machinery supplier/make |
| --- | --- | --- | --- |

### SIGNATURE OF THE TENDERER

SCHEDULE - G

DETAILS OF TESTING EQUIPMENT AVAILABLE AT REPAIR CENTRE                              (CRITICAL EQUIPMENT)

Name of the Tenderer:

Location/Place:

| Sl. No. | Name of the Test | Details of equipment available and used |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Name of the equipment | Make | Capacity/range | Model | Serial No. | Year of mfg | Date of calibration | Name of the lab calibrated | Remarks |

### SIGNATURE OF THE TENDERER

SCHEDULE – H

DETAILS OF POWER TRANSFORMERS MANUFACTURED/

REPAIRD SO FAR

| Sl. No. | Particulars of transformers | Manufacture/ repaired | Quantity | Due date of delivery | Actual date of delivery | To whom supplied/ Repairer |
| --- | --- | --- | --- | --- | --- | --- |
| A) | TGSPDCL |  |  |  |  |  |
| B) | TGTRANSCO/OTHER DISCOMS |  |  |  |  |  |
| C) | OTHERS (specify) |  |  |  |  |  |

Note:	Certificates issued not below the rank of Divisional Engineer shall be furnished by the bidder without fail, in support of the above information.

### SIGNATURE OF THE TENDERER

##### SCHEDULE – I

PARTICULARS OF POWR TRANSFORMERS UNDER MANUFACTURE/ REPAIRS/OVERHAULS UNDER EXECUTION

| Sl. No. | Particulars of Transformers | Quantity | Due date of delivery | To whom to be supplied/ repaired |
| --- | --- | --- | --- | --- |
| A) | TGSPDCL |  |  |  |
| B) | TGTRANSCO/OTHER DISCOMS |  |  |  |
| C) | OTHERS (specify) |  |  |  |

Note:	Certificates issued not below the rank of Divisional Engineer shall be furnished by the bidder without fail, in support of the above information.

### SIGNATURE OF THE TENDERER

##### SCHEDULE - J

##### DECLARATION FOR TAKING UP THE AWARDED WORKS

On award of work, I/We …………………………………………. will take up the works promptly and achieve progress as per the programme communicated for each of the work. If I/We …………………………………………. do not show the progress as per Schedule communicated for each work and the progress is (are) proved to be very slow which may result in delay in completion, the TGSPDCL can cancel all such works and may got be executed through alternate agencies at our cost and risk and without prejudice to the right of TGSPDCL to levy any penalties as per the terms of contract.

### SIGNATURE OF THE TENDERER

##### SCHEDULE – K

##### LIST OF MATERIALS FOR REPAIR/OVERHAUL OF

##### POWER TRANSFORMER WORKS

| Sl. No. | Name of the material | Make/ IS Standard | Source of Supply |
| --- | --- | --- | --- |
| 1) | Winding wire (Copper strip/ Conductors) |  |  |
| 2) | Core lamination (CRGO) |  |  |
| 3) | Insulation paper |  |  |
| 4) | OLTC |  |  |

Note:	The materials utilized for repair of Power Transformers i.e., Winding wire, Core laminations, OLTC, etc., should conform with the standards specified in IS:2026 for Power Transformers. The repairer should ensure that the material utilized for replacement of the defective parts should conform to the relevant Indian Standard Specification. In case of other items for which IS specification exists, the same shall be procured from such firms having ISI Certification. Items for which IS had not yet been framed the material shall be procured from the reputed and standard/TSTRANSCO approved manufacturers.

I/We hereby agree to supply the materials only from the reputed manufacturer/ supplier.

### SIGNATURE OF THE TENDERER

##### SCHEDULE – L

##### SELF DECLARATION

I/We…………………………………… do hereby express my/our willingness to undertake rate contract as per the conditions, standards, specifications, rules and regulations, etc., stipulated in the Tender at the rates indicated per unit against each item of the tender schedule.

I / We………………………………. have gone through carefully all the above and enclosed the necessary documents as indicated. I/We also solemnly declare that I/We will abide by the conditions contained in the Tender Schedules and for having not produced, or produced incorrect / false certificates and shall not claim for any relief/ relaxation thereafter.

### SIGNATURE OF THE TENDERER

##### SCHEDULE – M

CHECK LIST

COMMERICAL CONFIRMATIONS

State ‘Yes’ or ‘No’ to each of the following items

| Sl. No. | Particulars | Check list |
| --- | --- | --- |
| 1) | Whether Bid form enclosed | Yes / No |
| 2) | Whether Bid submitted in two parts i.e., - Pre Qualification Bid(Technical bid) - Price Bid | Yes / No |
| 3) | Whether Technical Bid enclosed in sealed cover | Yes / No |
| 4) | Whether qualification and performance particulars enclosed along with certificates | Yes / No |
| 5) | Whether performance statement enclosed | Yes / No |
| 6) | Whether details to be furnished by the manufacturer enclosed, if applicable | Yes / No |
| 7) | Whether Self declaration form enclosed | Yes / No |
| 8) | Whether all Schedules A-N enclosed | Yes / No |
| 9) | Whether proof of turnover enclosed | Yes / No |
| 10) | Whether previous repair/overhaul order copies enclosed | Yes / No |
| 11) | Whether bid security DD/BG enclosed | Yes / No |
| 12) | Whether all the required qualification criteria documents enclosed, | Yes / No |
| 13) | Whether 90 days validity is accepted | Yes / No |
| 14) | Whether TGSPDCL payment terms accepted | Yes / No |
| 15) | Whether Guarantee Clause accepted | Yes / No |
| 16) | Whether quoted prices are firm | Yes / No |
| 17) | Whether all particulars required for pre-qualification bid enclosed | Yes / No |
| 18) | Whether all the clauses accepted | Yes / No |

Note:	The tenderer shall indicate that all the forms and enclosures indicated in the checklist furnished along with the Bid and complied with.

### SIGNATURE OF THE TENDERER

SCHEDULE-N

Optimization of Turn around time of PTR Repairs (OTPR) Time Line

- Transportation of sick PTR to Repair Shed from failed location

The sick power transformer shall be lifted within 7 days from date of fixing of agency

- Joint Inspection of sick PTR

The Joint inspection shall be completed within 3 days from date of receipt of sick PTR at the repair shed & the Joint Inspection Report shall be uploaded in website by the repairer within 24 Hours & the same may be approved by DE/TRE within 3 days duly verifying the uploaded Joint Inspection Report.

- Completion of Repairs

The sick PTR shall be repaired within 60 days for PTRs of capacity upto 8 MVA and 90 days for PTRs of capacity above 8 MVA from date of issue of Job Order & kept ready for delivery which includes

  - Arrangement of Stage wise inspection of repairs before completion of Core Coil Assembly to ensure that the repair/overhaul works have been carried as per the Joint Inspection report and to check all items as per repair/overhaul estimate. Second inspection notes (Ensuring weights of winding according to issued Job order) along with photos are to be uploaded in web for carrying out further repair work.

  - The repairer shall invite for inspection after CCA and inspection notes shall be prepared uploaded in web.

  - Final testing of PTR to be carried out in presence of concerned DE/TRE & upload the Final test reports of the PTR duly approved by DE/TRE.

### SIGNATURE OF THE TENDERER

| FORMAT-I JOINT INSPECTION / ASSESSMENT ON SICK POWER TRANSFORMER |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| TGSPDCL: Circle Name |  |  |  |  |  |  |  |
| Repairing is at |  |  |  |  |  |  |  |
| Name & Address of PTR Repairing Unit |  |  |  |  |  |  |  |
| PTR failed at: |  |  |  | Date of Date of Failure: |  |  |  |
| Work Allotment Ref: |  |  |  |  |  |  |  |
| T Note No: |  |  | Date: |  |  |  |  |
| Joint Inspection Date: |  |  |  |  |  |  |  |
| Name Plate Details: |  |  |  |  |  |  |  |
| Rating: |  | KVA | Make: |  | Sl. No: |  |  |
| Voltage Ratio: | HV: | 33000 | KV | Rated Current | HV: |  | Amps |
|  | LV: | 11000 | KV |  | LV: |  | Amps |
| Vector Group: |  |  | Phases: |  | Frequency: |  | 50 HZ |
| Temp. Rise: |  |  | Cooling: |  | Tap Changer: |  |  |
| No. of Tappings: |  |  | Normal Tap: |  | %Impedance |  |  |
| Yr of mfg: |  | No-Load Losses (W): |  |  | Load Losses (W): |  |  |
| Main Tank Oil (Ltrs): |  |  |  | OLTC Oil (Ltrs): |  |  |  |
| Total Oil (Litres): |  |  |  | Oil Weight (Kg): |  |  |  |
| Core Weight (Kg): |  |  |  | Windings Weight (Kg): |  |  |  |
| Other parts Weight (Kg): |  |  |  | Total Wt of PTR (Kg): |  |  |  |
| Personnel Present: |  |  |  |  |  |  |  |
| From TGSPDCL |  |  |  | From PTR Repairing Unit |  |  |  |
| 1. Name |  |  |  | 1. Name |  |  |  |
| Designation |  |  |  | Designation |  |  |  |
| 2. Name |  |  |  | 2. Name |  |  |  |
| Designation |  |  |  | Designation |  |  |  |
| 3. Name |  |  |  | 3. Name |  |  |  |
| Designation |  |  |  | Designation |  |  |  |
| Transportation of PTR Done by: |  |  |  |  |  |  |  |
| In case Night halt Detailed reasons: |  |  |  |  |  |  |  |
| After Repairer Transportation of PTR to be done by: |  |  |  |  |  |  |  |
| OBSERVATIONS (For each replacement of material, damage/ failure details and detailed justification shall be mentioned and all removed materials shall be taken over by concerned DE/ Transformers duly mentioning in the Delivery Challan & Gate Pass of PTR Repairing Agency. Copies of Delivery Challan & Gate Pass Shall be enclosed along with Joint Inspection Report for issuing Job order. |  |  |  |  |  |  |  |
| 1 |  |  |  |  |  |  |  |
| 2 |  |  |  |  |  |  |  |
| 3 |  |  |  |  |  |  |  |
| 4 |  |  |  |  |  |  |  |
| 5 |  |  |  |  |  |  |  |
| 6 |  |  |  |  |  |  |  |
| 7 |  |  |  |  |  |  |  |
| 8 |  |  |  |  |  |  |  |
| 9 |  |  |  |  |  |  |  |
| 10 |  |  |  |  |  |  |  |
| ASSESSMENT |  |  |  |  |  |  |  |
| Providing of New HV Wdg: |  |  | Details of Damaged Wdg other than Tap Wdgs: |  |  |  |  |
| Strip Width with insulation |  |  | mm | Strep Thickness with insulation |  |  | mm |
| Bare Strip Width |  |  | mm | Bare Strip Thickness |  |  | mm |
| Cross Sectional Area of each strip |  |  |  | Sq.mm | No.of Parallels |  |  |
| Cross Sectional Area of winding |  |  |  | Sq.mm | Current Density (A/mm2) |  |  |
| Outer Diameter of Coil |  |  | mm | Inner Diameter of Coil |  |  | mm |
| Mean Dia of Coil |  |  | mm | Length of One Turn |  |  | mm |
| No.of Turns in one Disc |  |  |  | No.of Discs |  |  |  |
| No.of Turns |  |  | Length of Conductor in each phase |  |  |  | mm |
| Volume of Conductor in each phase |  |  |  | Cu.mm | Density |  | Kg/Cu.mm |
| Weight of Copper in each Phase |  |  |  | Kg |  |  |  |
| Weight of Copper in three Phases |  |  |  | Kgs |  |  |  |
| Details of Tap Windings to be replaced: |  |  |  |  |  |  |  |
| Strip Width with insulation |  |  | mm | Strep Thickness with insulation |  |  | mm |
| Bare Strip Width |  |  | mm | Bare Strip Thickness |  |  | mm |
| Cross Sectional Area of each strip |  |  |  | Sq.mm | No.of Parallels |  |  |
| Cross Sectional Area of winding |  |  |  | Sq.mm | Current Density (A/mm2) |  |  |
| Outer Diameter of Coil |  |  | mm | Inner Diameter of Coil |  |  | mm |
| Mean Dia of Coil |  |  | mm | Length of One Turn |  |  | mm |
| No.of Turns in one Disc |  |  |  | No.of Discs |  |  |  |
| No.of Turns |  | Length of Conductor from winding for Tap |  |  |  |  | mm |
| Length of Conductor in each phase |  |  |  | mm |  |  |  |
| Volume of Conductor in each phase |  |  |  | Cu.mm | Density |  | Kg/Cu.mm |
| Weight of Copper in each Phase |  |  |  | Kg |  |  |  |
| Weight of Copper in three Phases |  |  |  | Kgs |  |  |  |
| Total Weight of HV main & Tap Windings |  |  |  |  | Kgs |  |  |
| Height of HV Winding: |  |  | mm | Disc to Disc to Clearance: |  |  | mm |
| Providing of New LV Winding: |  |  |  | Details of Damaged Windings: |  |  |  |
| Strip Width with insulation |  |  | mm | Strep Thckness with insulation |  |  | mm |
| Bare Strip Width |  |  | mm | Bare Strip Thickness |  |  | mm |
| Cross Sectional Area of each strip |  |  |  | Sq.mm | No.of Parallels |  |  |
| Cross Sectional Area of winding |  |  |  | Sq.mm | Current Density (A/mm2) |  |  |
| Outer Diameter of Coil |  |  | mm | Inner Diameter of Coil |  |  | mm |
| Mean Dia of Coil |  |  | mm | Length of One Turn |  |  | mm |
| No.of Turns in one Disc |  |  |  | No.of Discs |  |  |  |
| No.of Turns |  |  | Length of Conductor in each phase |  |  |  | mm |
| Volume of Conductor in each phase |  |  |  | Cu.mm | Density |  | Kg/Cu.mm |
| Weight of Copper in each Phase |  |  |  | Kg |  |  |  |
| Weight of Copper in three Phases |  |  |  | Kg |  |  |  |
| Height of LV Winding: |  |  | mm | Disc to Disc to Clearance: |  |  | mm |
| Total Weight of Copper to be Replaced: |  |  |  |  | Kgs |  |  |
| PROVIDING OF RE-INSULATION |  |  |  |  |  |  |  |
| Remaining No.of Turns of HV Coil other than Tap windings in each Phase |  |  |  |  |  |  |  |
| Length of Conductor in each phase |  |  |  | mm |  |  |  |
| Volume of Conductor in each phase |  |  |  | Cu.mm | Density |  | Kg/Cu.mm |
| Weight of Copper in each Phase |  |  |  | Kg | Wt of HV |  | Kg |
| Remaining No.of Turns of HV Coil Tap windings in each Phase |  |  |  |  |  |  |  |
| Length of Concuctor from winding for Tap |  |  |  |  |  |  |  |
| Length of Conductor in each phase |  |  |  | mm |  |  |  |
| Volume of Conductor in each phase |  |  |  | Cu.mm | Density |  | Kg/Cu.mm |
| Weight of Copper in each Phase |  |  |  | Kg | Wt of HV |  | Kg |
| Total Weight of HV main & Tap Windings |  |  |  |  | Kgs |  |  |
| Remaining No.of Turns of LV Coil |  |  |  |  |  |  | mm |
| Length of LV Conductor in each phase |  |  |  |  |  |  |  |
| Volume of LV Conductor in each phase |  |  |  | Cu.mm | Density |  | Kg/Cu.mm |
| Weight of LV Copper in each Phase |  |  |  | Kg | Wt of HV |  | Kg |
| Total Weight of Copper to be Re-insulated: |  |  |  |  | Kgs |  |  |
| Weight of Windings as per Weighing Machine: |  |  |  |  |  |  |  |
| 1 | Weight of HV Winding in each Phase |  |  |  | Kgs |  |  |
| 2 | Weight of LV Winding in each Phase |  |  |  | Kgs |  |  |
| 3 | Total Weight of HV Windings |  |  |  | Kgs |  |  |
| 4 | Total Weight of LV Windings |  |  |  | Kgs |  |  |
| 5 | Weight of Paper Insulation & balance Oil in HV Windings |  |  |  |  |  | Kgs |
| 6 | Weight of Paper Insulation & balance Oil in LV Windings |  |  |  |  |  | Kgs |
| 7 | Weight of Paper Insulation & balance Oil in HV & LV Windings |  |  |  |  |  | Kgs |
| Core Details |  |  |  |  |  |  |  |
| Type of Core |  |  | Thickness of Core Plate: |  |  | mm |  |
| Diameter of Core |  |  | mm | No.of Steps: |  |  |  |
| 1st step Width |  |  | mm | 2nd Step Width |  |  | mm |
| 3rd Step width: |  |  | mm | 4th Step Width: |  |  | mm |
| 5th Step width: |  |  | mm | 6th Step Width: |  |  | mm |
| 7th Step width: |  |  | mm | 8th Step Width: |  |  | mm |
| 9th Step width: |  |  | mm | 10th Step Width: |  |  | mm |
| 11th Step width: |  |  | mm | 12th Step Width: |  |  | mm |
| Window Height |  |  | mm | Centre to Centre |  |  | mm |
| Weight of Top Yoke |  |  | Kg | Weight of Bottom Yoke: |  |  | Kg |
| Weight of Centre Limb: |  |  | Kg | Weight of one Side Limb: |  |  | Kg |
| Weight of Other side Limb: |  |  |  | Kg |  |  |  |
| Total Weight of Core: |  |  | Kg | Damaged Core Wt: |  |  | Kg |
| Tank Details: |  | Internal Dimensions: |  |  |  |  |  |
| Width: |  | mm |  | Length: |  | mm |  |
| Height: |  | mm |  | Volume: |  | Cu.mm |  |
| Conservator Tank Length: |  |  |  | mm | Diameter: |  | mm |
| No.of Radiators: |  |  | Oil Volume of Each Radiator: |  |  |  | Litres |
| Transformer Oil Requirement: |  |  |  |  |  |  |  |
| Main Tank Oil: |  |  | Litres | OLTC Oil: |  | Litres |  |
| Quantity of shortage Oil, In case Oil Gushedout/ Leakage at Substation and recorded in PTR failure Notification & Report and in T. Note (Notification, PTR Failure Report, T Note Copies clearly stating about oil gushedout/ leakage quantity along with detailed reasons shall be enclosed with Joint Inspection Report for issuing Job order.): |  |  |  |  |  |  | Litres |
| Filtration Losses 1% |  |  | Litres | Total Oil Requirement: |  |  | Litres |
| Quantity of Oil removed from the PTR before handing over to Repairing Agency:: |  |  |  |  |  |  | Litres |
| Quantity of Oil to be required i.e., Removed Oil qty, 1% Filtration Losses & above shortage Oil: |  |  |  |  |  |  | Litres |
| In case difference between Total Oil requirement and Quantity of Oil to be required, Detailed reasons and justification shall be submitted along with Joint Inspection Report to issue Job Order: Enclosed (mention YES or NO or NA) |  |  |  |  |  |  |  |
| Details of works to be carried out by PTR Repairing Agency along with detailed reasons and justification. |  |  |  |  |  |  |  |
| 1 |  |  |  |  |  |  |  |
| 2 |  |  |  |  |  |  |  |
| 3 |  |  |  |  |  |  |  |
| 4 |  |  |  |  |  |  |  |
| 5 |  |  |  |  |  |  |  |
| 6 |  |  |  |  |  |  |  |
| 7 |  |  |  |  |  |  |  |
| 8 |  |  |  |  |  |  |  |
| 9 |  |  |  |  |  |  |  |
| 10 |  |  |  |  |  |  |  |
| 11 |  |  |  |  |  |  |  |
| 12 |  |  |  |  |  |  |  |
| 13 |  |  |  |  |  |  |  |
| 14 |  |  |  |  |  |  |  |
| 15 |  |  |  |  |  |  |  |
| Tentative Reasons for failure of PTR: |  |  |  |  |  |  |  |
| It is certified that all removed defective, failed, and to be replaced materials are handedover by the PTR Repair Agency vide Delivery Challan No. …………………………… Dt: ……………………….., Gate Pass No. ………………………………… Dt: …………………………….. Vehicle No. ……………………………. And DE/ Transformers/ ....................................... received the materials in full shape. |  |  |  |  |  |  |  |
| From TGSPDCL |  |  |  | From PTR Repairing Unit |  |  |  |
| 1. Name |  |  |  | 1. Name |  |  |  |
| Designation |  |  |  | Designation |  |  |  |
| 2. Name |  |  |  | 2. Name |  |  |  |
| Designation |  |  |  | Designation |  |  |  |
| 3. Name |  |  |  | 3. Name |  |  |  |
| Designation |  |  |  | Designation |  |  |  |

| FORMAT-II |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Name of the PTR Repair Agency, Address |  |  |  |  |  |  |  |
| REPAIRED POWER TRANSFORMER TEST REPORT |  |  |  |  |  |  |  |
| (Tests as per Agreement Confirming to IS: 2026-1977) |  |  |  |  |  |  |  |
| TGSPDCL: Circle Name |  |  |  |  |  |  |  |
| PTR failed at: |  |  |  | Date of Testing: |  |  |  |
| Job order Ref: |  |  |  |  |  |  |  |
| Name Plate Details: |  |  |  |  |  |  |  |
| Rating: |  | KVA | Make: |  | Sl. No: |  |  |
| Voltage Ratio: | HV: |  | KV | Rated Current | HV: |  | Amps |
|  | LV: |  | KV |  | LV: |  | Amps |
| Vector Group: |  |  | Phases: |  | Frequency: |  | 50 HZ |
| Temp. Rise: |  |  | Cooling: |  | Tap Changer: |  |  |
| No. of Tappings: |  |  | Normal Tap: |  | %Impedance |  |  |
| Yr of mfg: |  | No-Load Losses (W): |  |  | Load Losses (W): |  |  |
| Main Tank Oil (Ltrs): |  |  |  | OLTC Oil (Ltrs): |  |  |  |
| Total Oil (Litres): |  |  |  | Oil Weight (Kg): |  |  |  |
| Core Weight (Kg): |  |  |  | Windings Weight (Kg): |  |  |  |
| Other parts Weight (Kg): |  |  |  | Total Wt of PTR (Kg): |  |  |  |
| Insulation Resistance Test results: |  |  |  |  |  |  |  |
| HV Winding to Earth (M Ohms): |  |  |  | LV winding to Earth (M Ohms): |  |  |  |
| HV winding to KV winding (M Ohms): |  |  |  | Temperature Centi Degrees: |  |  |  |
| Ratio Test: |  |  |  |  |  |  |  |
| Tap No. | Measured Values |  |  | % Deviation |  |  | Polarity & Phase Relationship |
|  | U Phase | V Phase | W Phase | U Phase | V Phase | W Phase |  |
| 1 |  |  |  |  |  |  |  |
| 2 |  |  |  |  |  |  |  |
| 3 |  |  |  |  |  |  |  |
| 4 |  |  |  |  |  |  |  |
| 5 |  |  |  |  |  |  |  |
| 6 |  |  |  |  |  |  |  |
| 7 |  |  |  |  |  |  |  |
| 8 |  |  |  |  |  |  |  |
| 9 |  |  |  |  |  |  |  |
| 10 |  |  |  |  |  |  |  |
| 11 |  |  |  |  |  |  |  |
| 12 |  |  |  |  |  |  |  |
| 13 |  |  |  |  |  |  |  |
| 14 |  |  |  |  |  |  |  |
| 15 |  |  |  |  |  |  |  |
| 16 |  |  |  |  |  |  |  |
| 17 |  |  |  |  |  |  |  |
| D C Resistance Measurement Test Results (both increasing taps & decreasing taps): |  |  |  |  |  |  |  |
| Winding Temperature in Centi Degrees: |  |  |  |  |  |  |  |
| LV Winding Resistance in milli-Ohms |  | u-v | v-w | w-u | u-n | v-n | w-n |
| HV Winding Resistance in Ohms: |  |  |  |  |  |  |  |
| Tap No. | Values while Raising Taps |  |  | Values while Lowering Taps |  |  | Difference (Yes / No) |
|  | U-V | V-W | W-U | U-V | V-W | W-U |  |
| 1 |  |  |  |  |  |  |  |
| 2 |  |  |  |  |  |  |  |
| 3 |  |  |  |  |  |  |  |
| 4 |  |  |  |  |  |  |  |
| 5 |  |  |  |  |  |  |  |
| 6 |  |  |  |  |  |  |  |
| 7 |  |  |  |  |  |  |  |
| 8 |  |  |  |  |  |  |  |
| 9 |  |  |  |  |  |  |  |
| 10 |  |  |  |  |  |  |  |
| 11 |  |  |  |  |  |  |  |
| 12 |  |  |  |  |  |  |  |
| 13 |  |  |  |  |  |  |  |
| 14 |  |  |  |  |  |  |  |
| 15 |  |  |  |  |  |  |  |
| 16 |  |  |  |  |  |  |  |
| 17 |  |  |  |  |  |  |  |
| Dielectric Tests: |  |  |  |  |  |  |  |
| Separate Source Voltage Withstand / HV / Power Frequency Test: |  |  |  |  |  |  |  |
| HV Winding to LV Winding, Core frame, Tank Earthed and applied Voltage for one minute |  |  | Voltage Applied |  | Current in milli-Amps | Withstood (Yes/ No) |  |
|  |  |  |  | KV |  |  |  |
| LV Winding to HV Winding, Core frame, Tank Earthed and applied Voltage for one minute |  |  | Voltage Applied |  | Current in milli-Amps | Withstood (Yes/ No) |  |
|  |  |  |  | KV |  |  |  |
| Induced Over Voltage/ DVDF Test: |  |  |  |  |  |  |  |
| Applied High Frequency Voltage on LV side keeping HV side open |  |  | Voltage Applied in KV | Current in Amps | Frequency in HZ | Time (Seconds) | Withstood (Yes/ No) |
| Open Circuit / No-Load Losses Test at Normal Tap: |  |  |  |  |  |  |  |
| Rated Voltage applied on LV Side keeping HV open, Recorded values displayed on Power Analyser |  |  |  |  |  |  |  |
| Average Values: |  |  |  |  |  |  |  |
| Voltage: |  | Volts |  | Power Factor: |  |  |  |
| Current: |  | Amps |  | Total Active Power: |  |  | Watts |
| Frequency: |  | HZ |  | Total Apparent Power: |  |  | VA |
| Phase Values: |  |  |  |  |  |  |  |
| V-1 |  | Volts | I-1 |  | Amps | PF-1 |  |
| V-2 |  | Volts | I-2 |  | Amps | PF-2 |  |
| V-3 |  | Volts | I-3 |  | Amps | PF-3 |  |
| W-1 |  | Watts | S-1 |  | VA |  |  |
| W-2 |  | Watts | S-2 |  | VA |  |  |
| W-3 |  | Watts | S-3 |  | VA |  |  |
| The Transformer is tested for Rated Voltage at all taps changing from Tap-1 to Tap-max (17). Found OK or NOT OK |  |  |  |  |  |  |  |
| Short Circuit Test at Normal Tap: |  |  |  |  |  |  |  |
| Voltage applied on HV side till rated current flow shorting LV shorted rigidly, Recorded values displayed on Power Analyser |  |  |  |  |  |  |  |
| Winding Temperature in Centi Degrees: |  |  |  |  |  |  |  |
| Average Values: |  |  |  |  |  |  |  |
| Voltage: |  | Volts |  | Power Factor: |  |  |  |
| Current: |  | Amps |  | Total Active Power: |  |  | Watts |
| Frequency: |  | HZ |  | Total Apparent Power: |  |  | VA |
| Phase Values: |  |  |  |  |  |  |  |
| V-1 |  | Volts | I-1 |  | Amps | PF-1 |  |
| V-2 |  | Volts | I-2 |  | Amps | PF-2 |  |
| V-3 |  | Volts | I-3 |  | Amps | PF-3 |  |
| W-1 |  | Watts | S-1 |  | VA |  |  |
| W-2 |  | Watts | S-2 |  | VA |  |  |
| W-3 |  | Watts | S-3 |  | VA |  |  |
| HV & LV winding phase and Neutral Currents in Amps measured with Clamp meter |  |  |  |  |  |  |  |
| HV Winding Currents |  |  |  | LV Winding Currents |  |  |  |
| I1 |  | Amps |  | I1 |  | Amps |  |
| I2 |  | Amps |  | I2 |  | Amps |  |
| I3 |  | Amps |  | I3 |  | Amps |  |
|  |  |  |  | In |  | Amps |  |
| The Transformer is tested for Rated Current at all taps changing from Tap-1 to Tap-max (17). Found OK or NOT OK |  |  |  |  |  |  |  |
| The OLTC is run continuously for eight cycles with motor and found OK or NOT OK |  |  |  |  |  |  |  |
| Magnetic Balance Test at Normal Tap: |  |  |  |  |  |  |  |
| 3 Phase LT Supply applied across |  | HV Side Voltage (Volts) |  |  | LV Side Voltage (Volts) |  |  |
|  |  | 1U-1V | 1V-1W | 1W-1U | 2u-2n | 2v-2n | 2w-2n |
| 1U | 1V |  |  |  |  |  |  |
| 1V | 1W |  |  |  |  |  |  |
| 1W | 1U |  |  |  |  |  |  |
| Magnetic Balance Test Results are Satisfactory (Yes/ No) |  |  |  |  |  |  |  |
| Vector Group Test: |  |  |  |  |  |  |  |
| LT 3 Phase Voltage applied on HV side (Volts) |  |  |  |  |  |  |  |
| 1U-1V |  | 1V-1W |  | 1W-1U |  |  |  |
| 1W-2w |  | 1V-2v |  | Is 1W-2w = 1V-2v: |  | Yes/No |  |
| 1W-2v |  | 1V-2w |  | Is 1W-2v > 1V-2w: |  | Yes/No |  |
| 2u-2n |  | 1V-2n |  | Is (1U-1V) = (2u-2n) + (1V-2n): |  | Yes/No |  |
| 1W-2w |  | 2w-2v |  | Is (1W-2v) = (1W-2w) + (2w-2v): |  | Yes/No |  |
| 1W-2v |  |  |  |  |  |  |  |
| Vector Group Test Results are Satisfactory (Yes/ No) |  |  |  |  |  |  |  |
| Oil BDV (Break Down Voltage) Test: |  |  |  |  |  |  |  |
| Oil BDV Voltage (KV) by keeping gap 2.5 mm and slowly increasing voltage |  |  |  |  |  |  |  |
| 1st time |  | 2nd time |  | 3rd time |  | 4th time |  |
| 6th time |  | Avg BDV: |  |  |  |  |  |
| Oil BDV Test Results are Satisfactory (Yes/ No) |  |  |  |  |  |  |  |
| Additional Name Plate and Details painted: |  |  |  |  |  |  |  |
| Name Plate welded properly (Yes/ No) |  |  |  |  |  |  |  |
| Name of the repairer |  |  |  |  |  |  |  |
| Delivered on |  |  |  |  |  |  |  |
| Repair Guarantee Period Valid upto |  |  |  |  |  |  |  |
| Tests on OLTC |  |  |  |  |  |  |  |
| Tests on OLTC Conducted (Yes/ No) |  |  |  |  |  |  |  |
| Test Results found satisfactory (Yes/ No) |  |  |  |  |  |  |  |
| Oil Pressure Test |  |  |  |  |  |  |  |
| Oil Pressure Tests Conducted (Yes/ No) |  |  |  |  |  |  |  |
| Test Results found satisfactory (Yes/ No) |  |  |  |  |  |  |  |
| Tan Delta Test on Windings (tan delta with capacitance) |  |  |  |  |  |  |  |
| Point | Frequency | Loss Angle | Current | Voltage | Capacitance | Dissipation Factor | Increase is (More/ Less) |
| 1 |  |  |  |  |  |  |  |
| 2 |  |  |  |  |  |  |  |
| 3 |  |  |  |  |  |  |  |
| 4 |  |  |  |  |  |  |  |
| 5 |  |  |  |  |  |  |  |
| 6 |  |  |  |  |  |  |  |
| 7 |  |  |  |  |  |  |  |
| 8 |  |  |  |  |  |  |  |
| 9 |  |  |  |  |  |  |  |
| 10 |  |  |  |  |  |  |  |
| Tan Delta Test Results Satisfactory (Yes/ No) |  |  |  |  |  |  |  |
| Frequency Response Analysis Test |  |  |  |  |  |  |  |
| Sweep frequency Response Analysis Test Results are found satisfactory (Yes/ No) |  |  |  |  |  |  |  |
| Furan Test |  |  |  |  |  |  |  |
| Furan Test Results are found satisfactory (Yes/ No) |  |  |  |  |  |  |  |
| Testing Equipment Availability |  |  |  |  |  |  |  |
| Testing Equipment List enclosed (Yes / No): |  |  |  |  |  |  |  |
| Tests Analysis Sheet enclosed (Yes/ No) |  |  |  |  |  |  |  |
| Specific Other Remarks if any: |  |  |  |  |  |  |  |
| Tested by |  |  |  |  | Witnessed by |  |  |