## last bus stop suraksha &ramnare
Schedule (WBS No.T-2432-07-05-01-01-001,T-2432-07-05-01-01-002 & T-2432-07-05-01-01-004 )
Name o f the work:Bifurcation of loads on 11KV Suraksha Enclave feeder emanating from 33/11KV Vemana Colony SS by erection of 1.77KM of new 11KV feeder from 33/11KV Vemana Colony SS & bifurcation of loads on 11KV Last bus-stop feeder & bifurcation of existing 11KV Ramnaresh Nagar of Kukatpally division and the work executed by the Construction wing of Kukatpally division of Medchal Circle.
Sl.No. | SSR CODES | Estimate Quantity (Only figures) | Particulars | Work Type eg., Earth Work, Electrical works..etc., (Upto 200 Characters) | Item Short Description | APSS/Morth CI.Number (Upto 200 characters) | Rate INR upto 2 Decimals | UOM (upto 50 Characters) | UOM (upto 50 Characters) | Amount INR (Upto 2 Decimals)
1 | SWR10454 | 3.98 | Stringing of HT AB Cable with GI Metal Parts HT AB Cable 11 KV 3x185+70 Sqmm | Electrical work | Electrical work | As per relevent standard specification | 41876.1 | KM | 41876.1 | 166666.878
2 | SMR11485 | 140 | Supply of earthing pipe with materials Supply of GI Flat 25X3 mm | Electrical work | Earthing work | As per relevent standard specification | 105 | KG | 105 | 14700
3 | SWR11039 | 46 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders)0.76 M x 0.76M x 1.83M(2.6" x 2.6" x 6.0") | Electrical work | Excavation work | As per relevent standard specification | 928 | EA | 928 | 42688
4 | SMR11504 | 32 | End Termination of AB cable (each lead):Supply of 11KV 5+70sq.mm/ 3x70+70sq.mm /3x35+35sq.mm AB cable end Kits | Electrical work | Electrical work | As per relevent standard specification | 950 | SET | 950 | 30400
5 | SWR10667 | 48 | End Termination of AB cable (each lead): 120 Sqmm to 185 Sqmm | Electrical work | Electrical work | As per relevent standard specification | 800 | EA | 800 | 38400
6 | SMR12099 | 213 | Supply and Erection of I Hook and Suspension Hook Supply of I Hook | Electrical work | Electrical work | As per relevent standard specification | 158 | EA | 158 | 33654
7 | SWR12099 | 213 | Supply and Erection of I Hook and Suspension Hook Erectionof I Hook | Electrical work | Electrical work | As per relevent standard specification | 55 | EA | 55 | 11715
8 | SMR40091 | 12 | Earthing of Sub-Station Supply of GI pipe 40 mm dia, 2 mtrs, 3mm thickness with bolts and nuts | Electrical work | Earthing work | As per relevent standard specification | 733 | EA | 733 | 8796
9 | SWR10357 | 12 | Providing of earthing with excavation of earth pit (0.6x0.6x2.4 Mts.) duly filling with bentonite, earth,running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.6M dia x 0.5 M height | Electrical work | Earthing work | As per relevent standard specification | 1234.2 | EA | 1234.2 | 14810.4
10 | SWR10671 | 10 | T' Branch KitErection of Assemble Kit for 'T' Branche | Electrical work | Elecrical work | As per relevent standard specification | 1800 | EA | 1800 | 18000
11 | SWR24971 | 10 | T' Branch Kit Supply and erection of T-Branch kit | Electrical work | Elecrical work | As per relevent standard specification | 3215 | EA | 3215 | 32150
12 | SWR10673 | 34 | Straight through joints of AB cable (each lead) Supply and ere Angle line Asmbly kits | Electrical work | Elecrical work | As per relevent standard specification | 2124 | EA | 2124 | 72216
13 | SWR11862 | 6 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels,current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)Above 20 Km and upto 30 Km with Lorry for each trip | Electrical work | Elecrical work | As per relevent standard specification | 3691.38 | EA | 3691.38 | 22148.28
14 | SWR12413 | 8 | LOADING of LINE MATERIALS 11 KV AB Cable (XLPE) 3 Core | Electrical work | Elecrical work | As per relevent standard specification | 584 | DR | 584 | 4672
15 | SWR12431 | 8 | UNLOADING of LINE MATERIALS 11 KV AB Cable (XLPE) 3 Cor | Electrical work | Elecrical work | As per relevent standard specification | 438 | DR | 438 | 3504
16 | SMR11488 | 175 | Supply of earthing pipe with materials Supply of GI Bolts & Nuts etc | Electrical work | Elecrical work | As per relevent standard specification | 117.5 | KG | 117.5 | 20562.5
17 | SMR40132 | 48 | Supply of 120 Sqmm Aluminium lugs | Electrical work | Elecrical work | As per relevent standard specification | 12.52 | EA | 12.52 | 600.96
18 | SWR10356 | 43.81 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc.Including the cost of cement | Electrical work | Elecrical work | As per relevent standard specification | 6579 | M3 | 6579 | 288225.99
19 | SWR10320 | 181 | Fabrication of materials including 2 coats of Red oxide paintingBack clamps with 50 x 6 mm MS Flat | Electrical work | Elecrical work | As per relevent standard specification | 15 | EA | 15 | 2715
20 | SWR10653 | 3 | Formation of Cut point for 11 KV Single Circuit line excluding pole erection and stays | Electrical work | Elecrical work | As per relevent standard specification | 1435.81 | EA | 1435.81 | 4307.43
21 | SWR10672 | 179 | Straight through joints of AB cable (each lead)Supply and ere Straight line Asmbly kits | Electrical work | Elecrical work | As per relevent standard specification | 1661 | EA | 1661 | 297319
22 | SWR10393 | 5 | Erection of AB Switch and aligment complete Erection of 11KV 400/200A Conventional type ABSwitch including fixing of cross angles and alignment complete | Electrical work | Elecrical work | As per relevent standard specification | 3200 | EA | 3200 | 16000
23 | SWR10343 | 39 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports,back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation.Erection of 9.1M Pole | Electrical work | Elecrical work | As per relevent standard specification | 2400 | EA | 2400 | 93600
24 | SWR20308 | 39 | Sub-transport of poles upto Workspot upto 10KM (Including loading and unloading)9.1 Mtrs long PSCC Poles | Electrical work | Elecrical work | As per relevent standard specification | 407.29 | EA | 407.29 | 15884.31
25 | SWR10666 | 1.86 | Stringing of LT AB Cable LT AB cable 3x70 + 1x16 + 1x50 | Electrical work | Elecrical work | As per relevent standard specification | 8450 | KM | 8450 | 15717
26 | SWR10642 | 8 | Fabrication of 175x85/150x75mm RS joist pieces upto 12.5 meters length by welding joint together by means of 50x6mm flat and MS channel on either side including the cost of consumable. | Electrical work | Elecrical work | As per relevent standard specification | 512.55 | EA | 512.55 | 4100.4
27 | SWR11720 | 15 | 11KV side arm 75x40mm Channel 65x65x6mm Angle | Electrical work | Elecrical work | As per relevent standard specification | 100 | EA | 100 | 1500
28 | SWR11040 | 14 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders)0.75 M x 0.9 M x 1.95 M | Electrical work | Elecrical work | As per relevent standard specification | 990.68 | EA | 990.68 | 13869.52
29 | SWR11266 | 8 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports,back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation.Boxpole 9/10/11Meter | Electrical work | Erection work | As per relevent standard specification | 2643.83 | EA | 2643.83 | 21150.64
30 | SWR11269 | 15 | Fixing of Side Arm along with Cross Arm including angle strut up to 5 feet 11KV | Electrical work | Elecrical work | As per relevent standard specification | 455 | EA | 455 | 6825
31 | SWR10640 | 8 | Painting of Poles.Painting of R.S Joist,Box poles including cross arms and clamps with one coat of red oxid and two coats of Al.paint including cost of paint and consumables | Electrical work | Painting work | As per relevent standard specification | 1132 | EA | 1132 | 9056
32 | SMR25160 | 18 | S-Insulating Piercing Connector | Electrical work | Elecrical work | As per relevent standard specification | 1050 | EA | 1050 | 18900
33 | SWR21914 | 18 | Erection of Insulated Connectors with covers | Electrical work | Elecrical work | As per relevent standard specification | 80 | EA | 80 | 1440
34 | SWR12125 | 160 | Providing of RCC collar to earth pit.Running of GI eartn flat of size 25X3mm from all metallic parts of channels, AB Switch, HG fuse set,DTr neutral and LT Distribution box and inter connection of earth pits etc complete | Electrical work | Earthing work | As per relevent standard specification | 14.03 | M | 14.03 | 2244.8
35 | SMR11486 | 12 | Supply of earthing pipe with materials Supply of GI wire No 8 | Electrical work | Earthing work | As per relevent standard specification | 105 | KG | 105 | 1260
36 | SWR10204 | 16 | LOADING of LINE MATERIALSR.S. Joists 175 x 85 mm | Electrical work | Loading work | As per relevent standard specification | 76 | EA | 76 | 1216
37 | SWR10522 | 16 | UNLOADING of LINE MATERIALS R.S. Joists 175 x 85 mm | Electrical work | Unloading work | As per relevent standard specification | 50 | EA | 50 | 800
38 | SWR10206 | 1.5 | LOADING of LINE MATERIALS MS Channel,Angles,Flats&Rods | Electrical work | Loading work | As per relevent standard specification | 221 | TO | 221 | 331.5
39 | SWR10524 | 1.5 | UNLOADING of LINE MATERIALS MS Channel,Angles,Flats&Rod | Electrical work | Unloading work | As per relevent standard specification | 185 | TO | 185 | 277.5
40 | SWR11248 | 45 | LOADING of LINE MATERIALS-11KV Polymer Pin Insulator-GI pin | Electrical work | Loading work | As per relevent standard specification | 1 | EA | 1 | 45
41 | SWR11249 | 45 | UNLOADING of LINE MATERIALS11KV Polymer Pin Insulator-GI pin | Electrical work | Unloading work | As per relevent standard specification | 1 | EA | 1 | 45
42 | SWR10298 | 32 | Cutting charges for MS Sections RS Joists 175 x 85 mm | Civil work | Civil work | As per relevent standard specification | 47 | EA | 47 | 1504
43 | SWR10238 | 5 | LOADING of LINE MATERIALS 11 KV AB SWCH Con 200/400 A | Electrical work | Loading work | As per relevent standard specification | 80 | EA | 80 | 400
44 | SWR10556 | 5 | UNLOADING of LINE MATERIALS 11 KV AB SWCH Con 200/400 A | Electrical work | Unlaoding work | As per relevent standard specification | 80 | EA | 80 | 400
45 | SWR11974 | 90 | Laying of XLPE UG cable Double Run including excavation of trench of size 600mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV from road level and cable separation with machine cut bricks horizontally for every 3 meters , providing of DWC/GI pipes wherever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth,levelling and removing the debris from the site inluding the cost of lead and lift etc.. (Second cable laying cost not Included) depth of the trench LT-0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs.11 KV 3x185 Sqmm Cable | Electrical work | Laying work | As per relevent standard specification | 631.06 | M | 631.06 | 56795.4
46 | SWR12006 | 20 | Raising of double run cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe)11 KV 3x185 Sqmm Cable | Electrical work | Raising work | As per relevent standard specification | 243.53 | M | 243.53 | 4870.6
47 | SWR11230 | 1 | LOADING of LINE MATERIALS -11/33KV XLPE UG cable all size | Electrical work | Loading work | As per relevent standard specification | 1024 | DR | 1024 | 1024
48 | SWR11231 | 1 | UNLOADING of LINE MATERIALS-11/33KV XLPE UG cable all size | Electrical work | Un Loading work | As per relevent standard specification | 1024 | DR | 1024 | 1024
49 | SWR10988 | 90 | Laying of 2nd cable in excavated trench | Electrical work | Laying work | As per relevent standard specification | 204.1 | M | 204.1 | 18369
50 | SWR10359 | 13 | Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50 M height | Civil work | Civil work | As per relevent standard specification | 386 | EA | 386 | 5018
51 | SWR11234 | 112 | LOADING of LINE MATERIALS - Unwinding 11KV AB cable(3C/75mm LT) | Electrical work | Loading of Work | As per relevent standard specification | 6 | EA | 6 | 672
52 | SWR11235 | 112 | UNLOADING of LINE MATERIALS-Unwinding 11KV AB cabl(3C/75mm LT | Electrical work | Unloading of Work | As per relevent standard specification | 6 | EA | 6 | 672
53 | SWR11180 | 6 | Sub-transport of poles upto Workspot upto 10KM (Including loading and unloading) 11 Mtrs long PSCC Poles | Electrical work | Sub-transport of work | As per relevent standard specification | 431.97 | KM | 431.97 | 2591.82
54 | SWR10978 | 6 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports,back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation of 11 M long PSCC pole | Electrical work | Erection work | As per relevent standard specification | 4336.85 | EA | 4336.85 | 26021.1
55 | SWR10348 | 7 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports,back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation. R.S. Joists 150 x 150 mm | Electrical work | Erection work | As per relevent standard specification | 1952.61 | EA | 1952.61 | 13668.27
56 | SWR10862 | 3.24 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels,current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)Above 20 Km and upto 30 Km with Lorry for each trip | Electrical work | Transportation of Work | As per relevent standard specification | 373 | EA | 373 | 1208.52
57 | SWR10461 | 1 | Erection of AB Switches, VCBs, LAs, PTs, CTs, DTRs etc Erection of 11 KV VCB with Control Panel | Electrical work | Erection work | As per relevent standard specification | 12000 | EA | 12000 | 12000
58 | SWR11879 | 360 | Control Cable Laying of 4 core/10 core 2.5 sq. mm.Copper control cable in aready excavation trench including cost of providing single compress glands at both ends . | Electrical work | Laying of work | As per relevent standard specification | 27 | EA | 27 | 9720
59 | SMR11487 | 30 | Supply of earthing pipe with materials Supply of MS bolts & nuts and washers etc of all sizes | Electrical work | Supply of Work | As per relevent standard specification | 91.25 | EA | 91.25 | 2737.5
60 | SWR11828 | 1 | provision for additional feeder on existing DC Announnciation pannel including material (technic push button along with elt) | Electrical work | Electrical work | As per relevent standard specification | 2500 | EA | 2500 | 2500
61 | SMR11482 | 7 | Supply of earthing pipe with materials iii)Supply of CI earth pipe 100 mm dia, 2.75 mt long thickness 10mm with flange as per specication | Electrical work | Earthing Work | As per relevent standard specification | 3486 | EA | 3486 | 24402
62 | SWR10357 | 7 | Providing of earthing with excavation of earth pit (0.6x0.6x2.4 Mts.) duly filling with bentonite, earth,running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.6M dia x 0.5 M height | Electrical work | Earthing Work | As per relevent standard specification | 1234.2 | EA | 1234.2 | 8639.4
63 | SWR10881 | 3 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied Painting of operating rods of 33kV, 11kV AB switches with post office red colour (including cost of paint) | Civil work | Painting work | As per relevent standard specification | 142 | EA | 142 | 426
64 | SWR10641 | 7 | Painting of R.S Joist,Box poles including cross arms and clamps with two coat of Al.paint including cost of paint and consumables. | Civil work | Painting work | As per relevent standard specification | 656 | EA | 656 | 4592
65 | SWR10133 | 3.92 | Transport of iron materials such as R.S. Joists, Rail Poles, fabricated supports, steel, iron, flat, M.S.Channels etc., by lorries. (excluding of loading & unloading )Above 20 KM and upto 30 KM | Transportationwork | Transportationwork | As per relevent standard specification | 476.34 | EA | 476.34 | 1867.2528
66 | SWR10199 | 1 | LOADING of LINE MATERIALS 11 KV VCBs&Panel boards | Electrical work | LoadingWork | As per relevent standard specification | 1024 | EA | 1024 | 1024
67 | SWR10517 | 1 | UNLOADING of LINE MATERIALS 11 KV VCBs&Panel boards | Electrical work | Unloading Work | As per relevent standard specification | 1044.48 | EA | 1044.48 | 1044.48
68 | SWR10205 | 7 | LOADING of LINE MATERIALS RSJoists150 x 150 mm/RailPole | Electrical work | LoadingWork | As per relevent standard specification | 176 | EA | 176 | 1232
69 | SWR10523 | 7 | UNLOADING of LINE MATERIALS RSJoists150 x150 mm/RailPol | Electrical work | Unloading Work | As per relevent standard specification | 107 | EA | 107 | 749
70 | SMR11916 | 12 | Supply of clamps as per IS 5561- 1970 , 12mm thickness with Alluminum and Alluminum alloy Supply of Alluminum alloy Pad clamps conforming to A6 of IS 617, 4bolted with hot dip galvanised bolts and double nuts with spring and flat washers of size M10 x 65 i.e(3/8" x 21/2 " to suit for panther ACSR/Zebra of pad size 75 X 75 X 15mm for carrying 600 A current rating . | Electrical work | Supply work | As per relevent standard specification | 227 | EA | 227 | 2724
71 | SWR10919 | 125 | Fabrication and connecting to risers from earth mat to structures, equipment,marshalling boxes, electrical panels, PLCC panels, fencing posts etc.M.S./ G.I. Flat 50x6mm / 50 x 8 mm ( Above ground) | Electrical work | Fabrication work | As per relevent standard specification | 41 | EA | 41 | 5125
72 | SWR10398 | 1 | Erection of AB Switches, VCBs, LAs, PTs, CTs, DTRs etc Erection of 11 KV LAS line type including earthing | Electrical work | Erection work | As per relevent standard specification | 505 | EA | 505 | 505
73 | SWR21241 | 1 | Hoisting of Insulators and hardware, stretching the conductor and stringing of 11 kV bus comprising of three phases with Single Zebra/panther conductor to a tension of 450kgs.(Bus section of 3.5mt) | Civil work | Civil work | As per relevent standard specification | 507 | EA | 507 | 507
74 | SWR20768 | 3.888 | Earth work excavation of in all soils except hard rock requiring blasting. | Electrical work | Earthing Work | As per relevent standard specification | 345 | EA | 345 | 1341.36
75 | SWR10732 | 1 | Con of Plinth for 11kv VCB 1.8x1.8x0.75m | Civil work | Civil work | As per relevent standard specification | 27629 | EA | 27629 | 27629
76 | SWR10391 | 6 | Making of Outdoor/Indoor End Termination 11 KV 3x300 Sqmm Cable | Electrical work | Electrical work | As per relevent standard specification | 2370.63 | EA | 2370.63 | 14223.78
77 | SWR11973 | 25 | Laying of XLPE UG cable Double Run including excavation of trench of size 600mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV from road level and cable separation with machine cut bricks horizontally for every 3 meters , providing of DWC/GI pipes wherever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and removing the debris from the site inluding the cost of lead and lift etc.. (Second cable laying cost not Included) depth of the trench LT-0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs.11 KV 3x300 Sqmm Cable | Electrical work | :Laying Work | As per relevent standard specification | 631.06 | EA | 631.06 | 15776.5
78 | SWR12005 | 30 | Raising of double run cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe)11 KV 3x300 Sqmm Cable |  |  | As per relevent standard specification | 275.4 | EA | 275.4 | 8262
79 | SWR10884 | 10 | Connection of equipment to bus and or another equipment with single zebra/Panther conductor including measuring, cutting,clamping and hoisting of suspension insulator assembly to support the conductor wherever necessary. | Electrical work | Electrical work | As per relevent standard specification | 224 | EA | 224 | 2240
80 | SWR10885 | 2 | Connection of equipment to bus and or another equipment with Twin zebra/Panther conductor including measuring, cutting,clamping and hoisting of suspension insulator assembly to support the conductor wherever necessary. | Electrical work | Electrical work | As per relevent standard specification | 3725.45 | EA | 3725 | 7450
81 | SWR33052 | 24 | S&Filling with Borrowed Gravel | Civil work | Civil work | As per relevent standard specification | 480 | EA | 480 | 11520
82 | SWR34472 | 24 | Seigniorage Charges - Gravel | Civil work | Civil work | As per relevent standard specification | 30 | EA | 30 | 720
83 | SMR11915 | 3 | Supply of Tension Hardware 3 Bolted for single Zebra/panther with 150 mm spacing. | Civil work | Civil work | As per relevent standard specification | 2055 | EA | 2055 | 6165
84 | SWR10920 | 31.91 | Laying of earth mat including excavation of trenches of depth 600mm,welding, connecting to equipment and connecting lightning shield to earth mat and earthing of fence posts, drilling and connecting earth rods including connecting cast iron pipes with the following sizes of MS Flats /GI Flats. including fabrication.75x 8mm MS Flat / GI Flat. | Electrical work | Laying Work | As per relevent standard specification | 65 | EA | 65 | 2074.15
85 | SWR10942 | 1 | Testing of Sub-Station Equipment Wirring, commissioning and testing of Outdoor Sub-station switchgear duly conducting the pre commissioning test as per relevent standards & issue of certificate by CEIG authorised testing Engineer | Electrical work | Electrical work | As per relevent standard specification | 1825 | EA | 1825 | 1825
86 | SWR22473 | 3 | Supply of various Clamps Supply of clamps as per IS 5561- 1970 , 12mm thickness with Alluminum and Alluminum alloy Supply of I Bolts | Electrical work | Supply Work | As per relevent standard specification | 294 | EA | 294 | 882
87 | SWR20904 | 6 | Breaker Supply & Providing of Panther T clamps. | Electrical work | Supply Work | As per relevent standard specification | 320 | EA | 320 | 1920
88 | SWR10294 | 50 | Cutting charges for MS Sections MS Channel 100 x 50 mm | Electrical work | Electrical work | As per relevent standard specification | 10 | EA | 10 | 500
89 | SWR10343 | 8 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports,back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation 9.1 M long PSCC pole | Electrical work | Erection of work | As per relevent standard specification | 2400 | EA | 2400 | 19200
90 | SWR11083 | 2 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports,back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation 9.1 M long PSCC poles for Strut | Electrical work | Erection of work | As per relevent standard specification | 2400 | EA | 2400 | 4800
91 | SWR11266 | 2 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation Box pole 9/10/11 Mtr | Electrical work | Erection of work | As per relevent standard specification | 2643.83 | EA | 2643.83 | 5287.66
92 | SWR10356 | 12.439 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc.Including the cost of cement | Electrical work | Mass concreting of work | As per relevent standard specification | 6579 | M3 | 6579 | 81836.181
93 | SWR11873 | 6 | Cutting charges for MS Sections MS Channel 75 x 40 mm | Electrical work |  | As per relevent standard specification | 9 | EA | 9 | 54
94 | SMR11487 | 30 | Supply of earthing pipe with materials Supply of MS bolts & nuts and washers etc of all sizes | Electrical work | Supply of work | As per relevent standard specification | 91.25 | KG | 91.25 | 2737.5
95 | SWR10393 | 2 | Erection of AB Switch and aligment complete Erection of 11KV 400/200A Conventional type AB Switch including fixing of cross angles and alignment complete | Electrical work | Erection of work | As per relevent standard specification | 3200 | EA | 3200 | 6400
96 | SWR10881 | 2 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1stgrade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied Painting of operating rods of 33kV, 11kV AB switches with post office red colour (including cost of paint) | Electrical work | Painting of work | As per relevent standard specification | 142 | EA | 142 | 284
97 | SMR40132 | 15 | Supply of 120 Sqmm Aluminium lugs | Electrical work | Supply of work | As per relevent standard specification | 12.52 | EA | 12.52 | 187.8
98 | SWR11039 | 8 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders)0.76 M x 0.76M x 1.83M (2.6" x 2.6" x 6.0") | Electrical work | Excavation of work | As per relevent standard specification | 928 | EA | 928 | 7424
99 | SWR10106 | 2 | Excavation of pits in all soils except hard rock requiring blasting 0.6 M x 0.9 M x 1.5 M | Electrical work | Excavation of work | As per relevent standard specification | 645 | EA | 645 | 1290
100 | SWR10108 | 7 | Excavation of pits in all soils except hard rock requiring blasting 0.75 M x 0.9 M x 1.95 M (1.31 cum) | Electrical work | Excavation of work | As per relevent standard specification | 629.85 | EA | 629.85 | 4408.95
101 | SWR10320 | 30 | Fabrication of materials including 2 coats of Red oxide painting Back clamps with 50 x 6 mm MS Flat | Electrical work | Fabrication work | As per relevent standard specification | 15 | EA | 15 | 450
102 | SWR10238 | 2 | LOADING of LINE MATERIALS 11 KV AB SWCH Con 200/400 A | Electrical work | Loading work | As per relevent standard specification | 80 | EA | 80 | 160
103 | SWR10556 | 2 | UNLOADING of LINE MATERIALS 11 KV AB SWCH Con 200/400 A | Electrical work | Unloading work | As per relevent standard specification | 80 | EA | 80 | 160
104 | SWR10454 | 1.7 | Stringing of HT AB Cable with GI Metal Parts HT AB Cable 11 KV 3x185+70 Sqmm | Electrical work | Stringing work | As per relevent standard specification | 41876.1 | KM | 41876.1 | 71189.37
105 | SMR11504 | 10 | End Termination of AB cable (each lead):Supply of 11KV 3x185+70sq.mm/3x70+70sq.mm/3x35+35sq.mm AB cable end Kits | Electrical work | Erection work | As per relevent standard specification | 950 | SET | 950 | 9500
106 | SWR10667 | 30 | End Termination of AB cable (each lead):120 Sqmm to 185 Sqmm | Electrical work | Erection work | As per relevent standard specification | 800 | EA | 800 | 24000
107 | SWR10673 | 14 | Straight through joints of AB cable (each lead)Supply and ere Angle line Asmbly kits | Electrical work | Erection work | As per relevent standard specification | 2124 | EA | 2124 | 29736
108 | SWR10672 | 54 | Straight through joints of AB cable (each lead) Supply and ere Straight line Asmbly kits | Electrical work | Erection work | As per relevent standard specification | 1661 | EA | 1661 | 89694
109 | SMR12099 | 70 | Supply and Erection of I Hook and Suspension Hook Supply of I hook | Electrical work | Supply work | As per relevent standard specification | 158 | EA | 158 | 11060
110 | SWR12099 | 70 | Supply and Erection of I Hook and Suspension Hook Erection of I hook | Electrical work | Supply work | As per relevent standard specification | 55 | EA | 55 | 3850
111 | SMR11485 | 20 | Supply of earthing pipe with materials Supply of GI Flat 25X3 mm | Electrical work | Supply work | As per relevent standard specification | 105 | KG | 105 | 2100
112 | SMR40091 | 2 | Earthing of Sub-Station Supply of GI pipe 40 mm dia, 2 mtrs, 3mm thickness with bolts and nuts | Electrical work | Earthing Work | As per relevent standard specification | 733 | EA | 733 | 1466
113 | SWR11863 | 3 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels,current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)Above 30 Km and upto 50 Km with Lorry for each trip | Electrical work | Transportation of work | As per relevent standard specification | 4372.74 | EA | 4372.74 | 13118.22
114 | SWR10131 | 1.35 | Transport of iron materials such as R.S. Joists, Rail Poles, fabricated supports, steel, iron, flat, M.S.Channels etc., by lorries. (excluding of loading & unloading )Upto 10 KM | Electrical work | Transportation of work | As per relevent standard specification | 339.66 | TO | 339.66 | 458.541
115 | SWR10365 | 0.07 | Paving out and stringing of conductor by providing temporary stays, tensioning, sagging correctly, fixing strain points, transferring to pin points binding, keeping stifner, rectification of poles, guys and jumpering etc., including transport of material from road side to location.55 Sqmm Single Circuit (3 Conductors) | Electrical work | Stringing work | As per relevent standard specification | 9454.86 | KM | 9454.86 | 661.8402
116 | SWR24971 | 4 | T-Branch kit Supply and erection of T-Branch kit | Electrical work | Supply work | As per relevent standard specification | 3215 | EA | 3215 | 12860
117 | SWR20308 | 10 | Sub-transport of poles upto Workspot upto 10KM (Including loading and unloading)9.1 Mtrs long PSCC Poles | Electrical work | Transportation work | As per relevent standard specification | 407.29 | EA | 407.29 | 4072.9
118 | SWR10653 | 2 | Formation of Cut points Formation of Cut point for 11 KV Single Circuit line excluding pole erection and stays | Electrical work | Erection work | As per relevent standard specification | 1435.81 | EA | 1435.81 | 2871.62
119 | SWR11180 | 5 | Sub-transport of poles upto Workspot upto 10KM (Including loading and unloading)11 Mtrs long PSCC Poles | Electrical work | Transportation work | As per relevent standard specification | 431.97 | EA | 431.97 | 2159.85
120 | SWR10357 | 2 | Providing of earthing with excavation of earth pit (0.6x0.6x2.4 Mts.) duly filling with bentonite, earth,running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.6M dia x 0.5 M height . | Electrical work | Earthing Work | As per relevent standard specification | 1234.2 | EA | 1234.2 | 2468.4
121 | SWR10359 | 2 | Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50 M height | Civil work | Civil work | As per relevent standard specification | 386 | EA | 386 | 772
122 | SWR10978 | 5 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports,back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation 11 Mtrs PSCC poles | Electrical work | Erection work | As per relevent standard specification | 4336.85 | EA | 4336.85 | 21684.25
Schedule Cost. (Excluding GST) | [9 empty] | 2107479.323