## Maisammaguda feeder
Schedule (WBS No.T-2432-07-05-01-02-001)
Schedule for bifurcation of existing 11KV Maisammaguda feeder emanating from 33/11KV G.P.Pally SS by proposing 1.80KM of new 11KV feeder from the same SS with stringing of 1.8KM of 55Sqmm. AAA Conductor on 11mts & 9.1Mtr PSCC poles & laying of 190 mtrs (D.Run) of 11KV XLPE 3X185Sqmm UG Cable duly erecting additional 1No. 11KV Bay & Breaker at 33/11KV G.P.Pally SS in G.P.Pally Section of Medchal Sub-Division of Medchal division and the work executed by Construction Division of Medchal Circle under T&D Improvement to Original Works (Summer Action Plan-2025 works)
11KV line
Sl.No. | SSR CODES |  | Particulars | Work Type eg., Earth Work, Electrical works..etc., (Upto 200 Characters) | Item Short Description | APSS/Morth CI.Number (Upto 200 characters) | Rate INR upto 2 Decimals | UOM (upto 50 Characters) | Amount INR (Upto 2 Decimals)
1 | SWR10365 | 1.8 | Paving out and stringing of conductor by providing temporary stays, tensioning, sagging correctly, fixing strain points, transferring to pin points binding, keeping stifner, rectification of poles, guys and jumpering etc., including transport of material from road side to location.55 Sqmm Single Circuit (3 Conductors) |  |  | 1.8 | KM | 9454.81 | 17018.66
2 | SWR10393 | 2 | Erection of AB Switch and aligment complete Erection of 11KV 400/200A Conventional type AB Switch including fixing of cross angles and alignment complete |  |  | 2 | EA | 3200 | 6400
3 | SWR10108 | 45 | Excavation of pits in all soils except hard rock requiring blasting 0.75 M x 0.9 M x 1.95 M (1.31 cum) |  |  | 45 | EA | 629.85 | 28343.25
4 | SWR10356 | 7.15 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand,Cement and curing etc.Including the cost of cement |  |  | 7.15 | M3 | 6579 | 47039.85
5 | SWR11862 | 2 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels,current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)Above 20 Km and upto 30 Km with Lorry for each trip |  |  | 2 | EA | 3691.38 | 7382.76
6 | SMR11487 | 100 | Supply of earthing pipe with materials Supply of MS bolts & nuts and washers etc of all sizes |  |  | 100 | KG | 91.25 | 9125
7 | SWR10294 | 100 | Cutting charges for MS Sections MS Channel 100 x 50 mm |  |  | 100 | EA | 10 | 1000
8 | SWR11180 | 45 | Sub-transport of poles upto Workspot upto 10KM (Including loading and unloading)11 Mtrs long PSCC Poles |  |  | 45 | EA | 431.97 | 19438.65
9 | SWR34252 | 10 | S&R 25x6mm GI Strip for Earthing |  |  | 10 | M | 113 | 1130
10 | SWR10978 | 45 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports,back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation 11 Mtrs PSCC poles |  |  | 45 | EA | 4336.85 | 195158.25
11 | SWR23200 | 1000 | Cut-Tree Branch(LT/11/33)&Trnsprt Debris |  |  | 1000 | EA | 4 | 4000
12 | SMR11482 | 4 | Supply of earthing pipe with materials iii)Supply of CI earth pipe 100 mm dia, 2.75 mt long thickness 10mm with flange as per specication |  |  | 4 | EA | 3486 | 13944
13 | SWR10357 | 4 | Providing of earthing with excavation of earth pit (0.6x0.6x2.4 Mts.) duly filling with bentonite, earth ,running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.6M dia x 0.5 M height . |  |  | 4 | EA | 1234.2 | 4936.8
14 | SWR11974 | 150 | Laying of XLPE UG cable Double Run including excavation of trench of size 600mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV from road level and cable separation with machine cut bricks horizontally for every 3meters , providing of DWC/GI pipes wherever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth,levelling and removing the debris from the site inluding the cost of lead and lift etc.. (Second cable laying cost not Included) depth of the trench LT-0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs.11 KV 3x185 Sqmm Cable |  |  | 150 | M | 631.06 | 94659
15 | SWR12006 | 40 | Raising of double run cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe)11 KV 3x185 Sqmm Cable |  |  | 40 | M | 243.53 | 9741.2
16 | SWR10390 | 8 | Making of Outdoor/Indoor End Termination 11 KV 3x185 Sqmm Cable |  |  | 8 | EA | 2370.63 | 18965.04
17 | SWR11313 | 0.8 | Restring-LT 3-Ph 34Sqmm-4 Conduct |  |  | 0.8 | KM | 7270 | 5816
18 | SWR10359 | 4 | Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50 M height |  |  | 4 | EA | 386 | 1544
19 | SWR10988 | 150 | Laying of the cable along the footpath through 225mm dia GI pipe for 33KV, 150mm dia GI pipe for 11KV (excluding the cost of GI pipe)Laying of 2nd cable in excavated trench |  |  | 150 | M | 204.1 | 30615
20 | SWR11308 | 0.8 | Restringing of existing loose Lines by removing the pin-binding and jumpers,Providing of temporary stays, providing stiffners pieces, replacement of damaged insulators, alignment of cross arms, pin binding and jumpering after tensioning and removing of the temporary stays complete .Restringing of with 55 Sqmm single ckt 3 cond |  |  | 0.8 | KM | 6616 | 5292.8
Schedule Cost. (Excluding GST) | [8 empty] | 521550.26
11KV BAY AND VCB
1 | SWR11266 |  | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports,back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation Box pole 9/10/11 Mtr |  |  | 3 | EA | 2643.83 | 7931.49
2 | SWR20768 |  | Earth work excavation of in all soils except hard rock requiring blasting. |  |  | 3.888 | M3 | 345 | 1341.36
3 | SWR10732 |  | Con of Plinth for 11kv VCB 1.8x1.8x0.75m |  |  | 1 | EA | 27629 | 27629
4 | SWR10461 |  | Erection of AB Switches, VCBs, LAs, PTs, CTs, DTRs etc Erection of 11 KV VCB with Control Panel |  |  | 1 | EA | 12000 | 12000
5 | SWR11040 |  | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders)0.75 M x 0.9 M x 1.95 M |  |  | 3 | EA | 990.68 | 2972.04
6 | SWR10393 |  | Erection of AB Switch and aligment complete Erection of 11KV 400/200A Conventional type AB Switch including fixing of cross angles and alignment complete |  |  | 4 | EA | 3200 | 12800
7 | SMR11482 |  | Supply of earthing pipe with materials iii)Supply of CI earth pipe 100 mm dia, 2.75 mt long thickness 10mm with flange as per specication |  |  | 4 | EA | 3486 | 13944
8 | SWR10357 |  | Providing of earthing with excavation of earth pit (0.6x0.6x2.4 Mts.) duly filling with bentonite, earth ,running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.6M dia x 0.5 M height . |  |  | 4 | EA | 1234.2 | 4936.8
9 | SMR11485 |  | Supply of earthing pipe with materials Supply of GI Flat 25X3 mm |  |  | 40 | KG | 105 | 4200
10 | SWR11879 |  | Laying of 4 core/10 core 2.5 sq. mm.Copper control cable in aready excavation trench including cost of providing single compress glands at both ends . |  |  | 550 | M | 27 | 14850
11 | SWR10917 |  | Fixing of Side Arm along with Cross Arm including angle strut up to 5 feet 11KV |  |  | 18 | EA | 65 | 1170
12 | SWR10869 |  | Fabrication of Main and Auxiliary structures with welding using raw steel such as RS joist, M.S.Angles, Plates, Channels, including the supply and fabrication of 6mm base plate to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection. |  |  | 1.05 | TO | 3426 | 3597.3
13 | SWR10133 |  | Transport of iron materials such as R.S. Joists, Rail Poles, fabricated supports, steel, iron, flat, M.S.Channels etc., by lorries. (excluding of loading & unloading )Above 20 KM and upto 30 KM |  |  | 3.22 | TO | 476.34 | 1533.81
14 | SWR11862 |  | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels,current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)Above 20 Km and upto 30 Km with Lorry for each trip |  |  | 1 | EA | 3691.38 | 3691.38
15 | SWR10920 |  | Laying of earth mat including excavation of trenches of depth 600mm,welding, connecting to equipment and connecting lightning shield to earth mat and earthing of fence posts, drilling and connecting earth rods including connecting cast iron pipes with the following sizes of MS Flats /GI Flats. including fabrication.75x 8mm MS Flat / GI Flat. |  |  | 25.53 | RMT | 65 | 1659.45
16 | SMR11486 |  | Supply of earthing pipe with materials iii)Supply of CI earth pipe 100 mm dia, 2.75 mt long thickness 10mm with flange as per specication |  |  | 10 | KG | 105 | 1050
17 | SWR10356 |  | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand,Cement and curing etc.Including the cost of cement |  |  | 3.15 | M3 | 6579 | 20723.85
18 | SMR11488 |  | Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50 M height |  |  | 25 | KG | 117.5 | 2937.5
19 | SWR10359 |  | Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50 M height |  |  | 4 | EA | 386 | 1544
20 | SWR11891 |  | Laying of earth mat including excavation of trenches of depth 600mm,welding, connecting to equipment and connecting lightning shield to earth mat and earthing of fence posts, drilling and connecting earth rods including connecting cast iron pipes with the following sizes of MS Flats /GI Flats. including fabrication.Connecting with GI Wire No.8 (Labour) |  |  | 10 | M | 14 | 140
21 | SWR12331 |  | Making of coil earthing pole with 8mm GI wireNut&Bolts for AB Switch |  |  | 4 | EA | 146.63 | 586.52
22 | SWR10881 |  | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied Painting of operating rods of 33kV, 11kV AB switches with post office red colour (including cost of paint) |  |  | 4 | EA | 142 | 568
23 | SWR10205 |  | LOADING of LINE MATERIALS RSJoists150 x 150 mm/RailPole |  |  | 3 | EA | 176 | 528
24 | SWR10523 |  | UNLOADING of LINE MATERIALS RSJoists150 x150 mm/RailPol |  |  | 3 | EA | 107 | 321
25 | SWR10199 |  | LOADING of LINE MATERIALS 11 KV VCBs&Panel boards |  |  | 1 | EA | 1024 | 1024
26 | SWR10517 |  | UNLOADING of LINE MATERIALS 11 KV VCBs&Panel boards |  |  | 1 | EA | 1044.48 | 1044.48
27 | SWR10238 |  | LOADING of LINE MATERIALS 11 KV AB SWCH Con 200/400 A |  |  | 4 | EA | 80 | 320
28 | SWR10556 |  | UNLOADING of LINE MATERIALS 11 KV AB SWCH Con 200/400 A |  |  | 4 | EA | 80 | 320
29 | SWR23105 |  | SS works L-PVC Control Cb 4, 10C |  |  | 550 | M | 1 | 550
30 | SWR23106 |  | SS works UL-PVC Control Cb 4, 10C |  |  | 550 | M | 0.15 | 82.5
31 | SWR10206 |  | LOADING of LINE MATERIALS MS Channel,Angles,Flats&Rods |  |  | 1.47 | TO | 221 | 324.87
32 | SWR10524 |  | UNLOADING of LINE MATERIALS MS Channel,Angles,Flats&Rod |  |  | 1.47 | TO | 185 | 271.95
33 | SWR10391 |  | Making of Outdoor/Indoor End Termination 11 KV 3x300 Sqmm Cable |  |  | 4 | EA | 2370.63 | 9482.52
34 | SWR10642 |  | Fabrication of 175x85/150x75mm RS joist pieces upto 12.5 meters length by welding joint together by means of 50x6mm flat and MS channel on either side including the cost of consumable. |  |  | 3 | EA | 512.55 | 1537.65
35 | SWR20863 |  | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports,back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation Erection of 5 Mts RS Joist (Bit) Pole including fixing of Pole Mounted Box |  |  | 2 | EA | 1044.23 | 2088.46
36 | SWR11973 |  | Laying of XLPE UG cable Double Run including excavation of trench of size 600mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV from road level and cable separation with machine cut bricks horizontally for every 3 meters , providing of DWC/GI pipes wherever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth,levelling and removing the debris from the site inluding the cost of lead and lift etc.. (Second cable laying cost not Included) depth of the trench LT-0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs.11 KV 3x300 Sqmm Cable |  |  | 50 | M | 631.06 | 31553
37 | SWR12005 |  | Raising of double run cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe)11 KV 3x300 Sqmm Cable |  |  | 20 | M | 275.4 | 5508
38 | SMR40011 |  | Supply of clamps as per IS 5561- 1970 , 12mm thickness with Alluminum and Alluminum alloy Supply of Alluminum alloy T clamps conforming to A6 of IS 617, 4 bolted with hot dip galvanised bolts and double nuts with spring and flat washers of size M10 x 65 i.e(3/8" x 21/2 " to suit for panther ACSR on all three ways /on one side and Zebra ACSR on take off side or any other combination for carrying 800 A current rating |  |  | 6 | EA | 299 | 1794
39 | SWR10884 |  | Bus Stringing Connection of equipment to bus and or another equipment with single zebra/Panther conductor including measuring, cutting,clamping and hoisting of suspension insulator assembly to support the conductor wherever necessary. |  |  | 2 | EA | 224 | 448
40 | SWR10988 |  | Laying of the cable along the footpath through 225mm dia GI pipe for 33KV, 150mm dia GI pipe for 11KV (excluding the cost of GI pipe)11 KV 3x185 Sqmm Cable |  |  | 50 | M | 204.1 | 10205
Schedule Cost. (Excluding GST) | [8 empty] | 209209.93
shifting 11KV OH line in Ss
1 | SWR10390 |  | Making of Outdoor/Indoor End Termination 11 KV 3x185 Sqmm Cable |  |  | 8 | EA | 2370.63 | 18965.04
2 | SWR11320 |  | Dismantling of Damaged Poles, not required and available in the middle of roads, transporting to stock point etc.Dism of 9.1M PSCC Pole |  |  | 2 | EA | 948.09 | 1896.18
3 | SWR11324 |  | Dismantling of Damaged Poles, not required and available in the middle of roads, transporting to stock point etc Dism of RS Joists 175 x 85 mm |  |  | 2 | EA | 1116 | 2232
4 | SWR22065 |  | LT lines : Dismantling of 11kV 34/ 55 Sqmm SC |  |  | 0.2 | KM | 4500 | 900
5 | SWR11974 |  | Laying of XLPE UG cable Double Run including excavation of trench of size 600mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV from road level and cable separation with machine cut bricks horizontally for every 3 meters , providing of DWC/GI pipes wherever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth,levelling and removing the debris from the site inluding the cost of lead and lift etc.. (Second cable laying cost not Included) depth of the trench LT-0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs.11 KV 3x185 Sqmm Cable |  |  | 160 | M | 631.06 | 100969.6
6 | SWR12006 |  | Raising of double run cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe)-11 KV 3x185 Sqmm Cable |  |  | 40 | M | 243.53 | 9741.2
7 | SWR20863 |  | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports,back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation Erection of 5 Mts RS Joist (Bit) Pole including fixing of Pole Mounted Box |  |  | 2 | EA | 1044.23 | 2088.46
8 | SWR10988 |  | Laying of the cable along the footpath through 225mm dia GI pipe for 33KV, 150mm dia GI pipe for 11KV (excluding the cost of GI pipe)Laying of 2nd cable in excavated trench |  |  | 160 | M | 204.1 | 32656
Schedule Cost. (Excluding GST) | [8 empty] | 169448.48
|  |  | Total Schedule Cost. (Excluding GST) |  |  | 900208.67
|  |  | GST@18% |  |  | 162037.5606
|  |  | Total Schedule Cost |  |  | 1062246.2306

## Kailash Hills Feeder
Schedule (WBS No.T-2432-07-05-01-02-002)
Schedule for proposal for providing of 820mtrs of new 11KV feeder from 33/11KV Shamshiguda SS with stringing of 820mtrs of 11KV 3X185+70Sq.mm.AB cable over now proposed 9.1mtr PSCC poles and existing Poles along with erection of 1No. 11KV Bay & Breaker for bifurcation existing 11KV Kailash Hills feeder emanating from 33/11KV Shamshiguda SS in Gajularamaram Section of Quthbullapur Sub-Division of Medchal Division and the work executed by the Construction Division of Medchal Circle under T&D Improvements to original works under Summer Action Plan-2024-2025 - Estimate Submitted - Reg.
11KV BAy Extension Materials
Sl.No. | SSR CODES | Particulars | Qty | Rate in Rs. | Per Unit | Amount in Rs.
1 | SWR10461 | Erection of AB Switches, VCBs, LAs, PTs, CTs, DTRs etc Erection of 11 KV VCB with Control Panel | 1 | EA | 12000 | 12000
2 | SMR11482 | Supply of earthing pipe with materials iii)Supply of CI earth pipe 100 mm dia, 2.75 mt long thickness 10mm with flange as per specication | 3 | EA | 3486 | 10458
3 | SWR10356 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand,Cement and curing etc.Including the cost of cement | 8.4 | M3 | 6579 | 55263.6
4 | SWR11879 | Laying of 4 core/10 core 2.5 sq. mm.Copper control cable in aready excavation trench including cost of providing single compress glands at both ends . | 350 | M | 27 | 9450
5 | SMR11488 | Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50 M height | 100 | KG | 117.5 | 11750
6 | SWR10942 | Testing of Sub-Station Equipment Wirring, commissioning and testing of Outdoor Sub-station switchgear duly conducting the pre commissioning test as per relevent standards & issue of certificate by CEIG authorised testing Engineer | 1 | EA | 1825 | 1825
7 | SWR12092 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders)(0.75M x 0.75M x 2.5M) 1.406 cum | 3 | EA | 1063.35 | 3190.05
8 | SWR10238 | LOADING of LINE MATERIALS11 KV AB SWCH Con 200/400 A | 2 | EA | 80 | 160
9 | SMR40025 | Supply of clamps as per IS 5561- 1970 , 12mm thickness with Alluminum and Alluminum alloy Supply of Alluminum PT clamps conforming to A6 of IS 617, with hot dip galvanised bolts and nuts suitable for single zebra / Panther | 3 | EA | 368 | 1104
10 | SMR40070 | Earth rods with (1) reputed make ISI PVC pipe of 5 feet length, 3 mm thickness, 32 mm dia inside cane wood stick closed both top & bottom ends with caps, (2) reputed make ISI (Finolex/ Polycab/ Havells) first quality flexible PVC wire of 6 Sq.mm multi-strand copper 10 Mtrs length one side crimped with a suitable copper lug, other side fixed with a lug, bolt & nut to a suitable 3 inch long copper heavy duty crocodile clip having insulated sleeves, (3) Copper flat of size 25 mm width 3 mm thick 250 mm length make hook shape fixed to the PVC pipe with 2 No.s 6 mm dia 65 mm length hot dip galvanized bolts triple nuts with a 2 mm thick spring washer and 1 mm thick 4 flat washers and fixing of the copper wire to the bolts with lugs.Danger boards with clamps | 1 | EA | 116 | 116
11 | SWR10917 | Labour for Fixing of all types of clamps | 21 | EA | 65 | 1365
12 | SWR10393 | Erection of AB Switch and aligment complete Erection of 11KV 400/200A Conventional type AB Switch including fixing of cross angles and alignment complete | 2 | EA | 3200 | 6400
13 | SWR11861 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels,current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading) Note: 1). It will be treated as full load of 10 MT and paid for 10 MT. 2). For 3 Ton vehicle : 50% of the following rates Above 10 Km and upto 20 Km with Lorry for each trip | 2 | EA | 3299.7 | 6599.4
14 | SWR10199 | LOADING of LINE MATERIALS 11 KV VCBs&Panel boards | 1 | EA | 1024 | 1024
15 | SWR10517 | UNLOADING of LINE MATERIALS 11 KV VCBs&Panel boards | 1 | EA | 1044.48 | 1044.48
16 | SWR10556 | UNLOADING of LINE MATERIALS 11 KV AB SWCH Con 200/400 A | 2 | EA | 80 | 160
17 | SWR10348 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports,back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation R.S. Joists 150 x 150 mm | 3 | EA | 1952.61 | 5857.83
18 | SMR11482 | Supply of earthing pipe with materials, Supply of CI earth pipe 100 mm dia, 2.75 mt long thickness 10mm with flange as per specication | 3 | EA | 3486 | 10458
19 | SWR10205 | LOADING of LINE MATERIALS RSJoists150 x 150 mm/RailPole | 3 | EA | 176 | 528
20 | SWR10523 | UNLOADING of LINE MATERIALS RSJoists150 x150 mm/RailPol | 3 | EA | 107 | 321
21 | SWR10206 | LOADING of LINE MATERIALS MS Channel,Angles,Flats&Rods | 1.5 | TO | 221 | 331.5
22 | SWR10524 | UNLOADING of LINE MATERIALS MS Channel,Angles,Flats&Rod | 1.5 | TO | 185 | 277.5
23 | SWR10265 | LOADING of LINE MATERIALS 11 KV, 10 KA LAs Line type | 3 | EA | 32 | 96
24 | SWR10583 | UNLOADING of LINE MATERIALS 11 KV, 10 KA LAs Line type | 3 | EA | 32 | 96
25 | SWR11701 | LOADING of LINE MATERIALS - PVC Control Cable 10C | 350 | M | 1 | 350
26 | SWR11712 | UNLOADING of LINE MATERIALS - PVC Control Cable 10C | 350 | M | 1.02 | 357
27 | SWR10297 | Cutting charges for MS Sections RS Joists 150 x 150 mm | 9 | EA | 48 | 432
28 | SWR10307 | Drilling of holes upto 20 mm dia using power drills MS Channel, Angles and flat | 120 | EA | 4 | 480
29 | SWR10359 | Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50 M height | 3 | EA | 386 | 1158
30 | SWR12294 | Excavatin of pit Providing of Base Concreting (Pole pits- 076 M x 0.76M x 0.15M ) with 1:3:6 Concrete Mix including curing with water | 0.25 | M3 | 5053 | 1263.25
31 | SWR10868 | Fabrication of Main and Auxiliary structures with power drilling using raw steel such as M.S.Angles, Plates, Channels, R.S.Joists, including the supply and fabrication of 6mm base and top plate for Box pole to the RSJoist poles excluding cost of Mild Steel and transport charges to substation site, including erection. | 1.5 | TO | 6852 | 10278
32 | SWR10867 | Alligning the Main and Auxiliary structures such as RS joist, M.S.Angles,Plates, Channels, Structure to zero level duly leveling in prefabricated MS frames with Hydraulic jacks before galvanising/ fabrication. | 1.5 | TO | 1470 | 2205
33 | SWR21241 | Hoisting of Insulators and hardware, stretching the conductor and stringing of 11 kV bus comprising of three phases with Single Zebra/panther conductor to a tension of 450kgs.(Bus section of 3.5mt) | 1 | EA | 507 | 507
34 | SMR11915 | Supply of Tension Hardware 3 Bolted for single Zebra/panther with 150 mm spacing. | 6 | SET | 2055 | 12330
35 | SWR11890 | Mass Concreting for pole Coping of 1.5'x1.5'x1 with 1:8 slope Using form boxes (0.031Cumt.) | 0.093 | M3 | 3893.01 | 362.05
36 | SMR40011 | Supply of clamps as per IS 5561- 1970 , 12mm thickness with Alluminum and Alluminum alloy Supply of Alluminum alloy T clamps conforming to A6 of IS 617, 4 bolted with hot dip galvanised bolts and double nuts with spring and flat washers of size M10 x 65 i.e(3/8" x 21/2 " to suit for panther ACSR on all three ways /on one side and Zebra ACSR on take off side or any other combination for carrying 800 A current rating | 9 | EA | 299 | 2691
37 | SMR22473 | Supply of clamps as per IS 5561- 1970 , 12mm thickness with Alluminum and Alluminum alloy Supply of I Bolts | 3 | EA | 294 | 882
38 | SMR40009 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1stgrade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied Supply of material cost for First coat of 1st Grade Aluminium Paint,brushes etc. | 2.8 | TO | 2181 | 6106.8
39 | SWR10877 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1stgrade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied Labour charges for painting including scratching and cleaning of Substationstructures of 1st coat of Aluminium | 2.8 | TO | 851 | 2382.8
40 | SMR40010 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1stgrade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied (*)Supply of material cost for Second coat of 1st Grade Aluminium Paint brushes, etc. | 2.8 | TO | 1293 | 3620.4
41 | SWR10879 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1stgrade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied Labour charges for painting including scratching and cleaning of Substation structures of 2nd coat of Aluminium . | 2.8 | TO | 482 | 1349.6
42 | SWR10920 | Laying of earth mat including excavation of trenches of depth 600mm,welding, connecting to equipment and connecting lightning shield to earth mat and earthing of fence posts, drilling and connecting earth rods including connecting cast iron pipes with the following sizes of MS Flats /GI Flats. including fabrication.75x 8mm MS Flat / GI Flat. | 20 | RMT | 65 | 1300
43 | SWR10919 | Fabrication and connecting to risers from earth mat to structures, equipment,marshalling boxes, electrical panels, PLCC panels, fencing posts etc.M.S./ G.I. Flat 50x6mm / 50 x 8 mm ( Above ground) | 50 | RMT | 41 | 2050
44 | SWR12510 | L-Cable Termination to Switchgear | 100 | EA | 27 | 2700
45 | SWR11089 | Painting of poles Paint of coping with 2 coats of white cement incl cost of paints etc. | 5 | EA | 48 | 240
46 | SWR12331 | Making of coil earthing pole with 8mm GI wireNut&Bolts for AB Switch | 2 | EA | 146.63 | 293.26
47 | SWR10881 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied Painting of operating rods of 33kV, 11kV AB switches with post office red colour (including cost of paint) | 2 | EA | 142 | 284
48 | SWR10860 | Supply & spreading of 20mm machine crushed metal (HBG) including cost of conveneyance of all materials, labour charges etc complete for finished item of work and directed by the engineer incharge | 5.5 | M3 | 2113 | 11621.5
49 | SWR10743 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied Painting of all suppports to a height of 0.3m coping with bituminous paint (black colour) and painting of coping with two coats of white cement (including cost of paint) | 3 | EA | 686 | 2058
50 | SWR10357 | Providing of earthing with excavation of earth pit (0.6x0.6x2.4 Mts.) duly filling with bentonite, earth ,running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.6M dia x 0.5 M height . | 3 | EA | 1234.2 | 3702.6
51 | SMR11485 | Supply of earthing pipe with materials. Supply of GI Flat 25X3 mm | 10 | KG | 105 | 1050
52 | SMR11435 | PROTECTION WORK Supply of Plain switches | 2 | EA | 30 | 60
53 | SWR11435 | PROTECTION WORK Fixing of Plain switches | 2 | EA | 13 | 26
54 | SMR11524 | PROTECTION WORK Supply of Indication LED Lamps 250 V DC (White,blue, Amber) Diameter 22.5 mm suitable for fixing in Control Relay Panels of Circuit Breakers. | 4 | EA | 130 | 520
55 | SMR11914 | PROTECTION WORK Supply of Push buttons (with NO contact) self illuminating LED 250 V DC White Diameter 22.5 mm suitable for fixing in Tripping Circuit Healthy Circuit in Control Relay Panels of Circuit Breakers. 220VDC Illuminating Healthy Trip Push Button | 2 | EA | 300 | 600
56 | SWR11380 | Fixing of Hylam Sheet & Cutting of Panel & Fixing of relay | 1 | EA | 2000 | 2000
Schedule Cost. (Excluding GST) | [5 empty] | 215135.62
11KV Line Material
1 | SWR10393 | Erection of AB Switch and aligment complete Erection of 11KV 400/200A Conventional type AB Switch including fixing of cross angles and alignment complete | 3 | EA | 3200 | 9600
2 | SWR10881 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied Painting of operating rods of 33kV, 11kV AB switches with post office red colour (including cost of paint) | 2 | EA | 142 | 284
3 | SWR12331 | Making of coil earthing pole with 8mm GI wireNut&Bolts for AB Switch | 2 | EA | 146.63 | 293.26
4 | SMR40091 | Earthing of Sub-Station Supply of GI pipe 40 mm dia, 2 mtrs, 3mm thickness with bolts and nuts | 5 | EA | 733 | 3665
5 | SWR10357 | Providing of earthing with excavation of earth pit (0.6x0.6x2.4 Mts.) duly filling with bentonite, earth ,running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.6M dia x 0.5 M height . | 5 | EA | 1234.2 | 6171
6 | SWR10356 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand,Cement and curing etc.Including the cost of cement | 3.3 | M3 | 6579 | 21710.7
7 | SMR11488 | Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50 M height | 50 | KG | 117.5 | 5875
8 | SMR40133 | S-185Sqmm Alluminium Lug | 15 | EA | 13 | 195
9 | SWR10319 | Fabrication of materials including 2 coats of Red oxide painting Back clamps with 75 x 8 mm MS Flat | 20 | EA | 31 | 620
10 | SWR10238 | LOADING of LINE MATERIALS 11 KV AB SWCH Con 200/400 A | 2 | EA | 80 | 160
11 | SWR10556 | UNLOADING of LINE MATERIALS 11 KV AB SWCH Con 200/400 A | 2 | EA | 80 | 160
12 | SWR10343 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports,back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation 9.1 M long PSCC pole | 6 | EA | 2400 | 14400
13 | SWR10107 | Excavation of pits in all soils except hard rock requiring blasting 0.76 M x 0.76M x 1.83M (2.6" x 2.6" x 6.0") 1.05 cum | 6 | EA | 700 | 4200
14 | SWR20308 | Sub-transport of poles upto Workspot upto 10KM (Including loading and unloading)9.1 Mtrs long PSCC Poles | 6 | EA | 407.29 | 2443.74
15 | SWR24971 | Supply and erection of T-Branch kit | 3 | EA | 3215 | 9645
16 | SMR11504 | End Termination of AB cable (each lead):Supply of 11KV 3x185+70sq.mm/3x70+70sq.mm/3x35+35sq.mm AB cable end Kits | 12 | SET | 950 | 11400
17 | SWR10667 | End Termination of AB cable (each lead):120 Sqmm to 185 Sqmm | 12 | EA | 800 | 9600
18 | SWR10673 | Straight through joints of AB cable (each lead)Supply and ere Angle line Asmbly kits | 16 | EA | 2124 | 33984
19 | SMR12099 | Supply and Erection of I Hook and Suspension Hook Supply- I Hook | 46 | EA | 158 | 7268
20 | SWR12099 | Supply and Erection of I Hook and Suspension Hook Erection- I Hook | 46 | EA | 55 | 2530
21 | SWR10454 | Stringing of HT AB Cable with GI Metal Parts HT AB Cable 11 KV 3x185+70 Sqmm | 0.82 | KM | 41876.1 | 34338.4
22 | SWR10672 | Straight through joints of AB cable (each lead)Supply and ere Straight line Asmbly kits | 30 | EA | 1661 | 49830
23 | SMR11485 | Supply of earthing pipe with materials Supply of GI Flat 25X3 mm | 50 | KG | 105 | 5250
24 | SWR10206 | LOADING of LINE MATERIALS MS Channel,Angles,Flats&Rods | 1 | TO | 221 | 221
25 | SWR10524 | UNLOADING of LINE MATERIALS MS Channel,Angles,Flats&Rod | 1 | TO | 185 | 185
26 | SWR12413 | LOADING of LINE MATERIALS 11 KV AB Cable (XLPE) 3 Core | 1 | DR | 584 | 584
27 | SWR12431 | UNLOADING of LINE MATERIALS 11 KV AB Cable (XLPE) 3 Cor | 1 | DR | 438 | 438
28 | SWR11234 | LOADING of LINE MATERIALS - Unwinding 11KV AB cable(3C/75mm LT) | 320 | M | 6 | 1920
29 | SWR11235 | LOADING of LINE MATERIALS - Unwinding 11KV AB cabl(3C/75mm LT | 320 | M | 6 | 1920
30 | SWR11248 | LOADING of LINE MATERIALS - 11KV Polymer Pin Insulator-GI pin | 24 | EA | 1 | 24
31 | SWR11249 | UNLOADING of LINE MATERIALS - 11KV Polymer Pin Insulator-GI pin | 24 | EA | 1 | 24
32 | SWR10294 | Cutting charges for MS Sections MS Channel 100 x 50 mm | 10 | EA | 10 | 100
33 | SWR10301 | Cutting charges for MS Sections MS flat of all sizes | 30 | EA | 2 | 60
34 | SWR10320 | Fabrication of materials including 2 coats of Red oxide painting Back clamps with 50 x 6 mm MS Flat | 20 | EA | 15 | 300
35 | SWR11720 | 11KV side arm 75x40mm Channel 65x65x6mm Angle | 4 | EA | 100 | 400
36 | SWR11269 | Fixing of Side Arm along with Cross Arm including angle strut up to 5 feet 11KV | 4 | EA | 455 | 1820
37 | SWR10671 | T Branch Kit Erection of Assemble Kit for 'T' Branche | 3 | EA | 1800 | 5400
38 | SWR21914 | Supply and Erection of I Hook and Suspension Hook Erection of Insulated Connectors with covers | 6 | EA | 80 | 480
39 | SMR25160 | S-Insulating Piercing Connector | 6 | EA | 1050 | 6300
40 | SWR12125 | Running of GI eartn flat of size 25X3mm from all metallic parts of channels, AB Switch, HG fuse set,DTr neutral and LT Distribution box and inter connection of earth pits etc complete | 50 | M | 14.03 | 701.5
41 | SMR11486 | Supply of earthing pipe with materials Supply of GI wire No 8 | 6 | KG | 105 | 630
Schedule Cost. (Excluding GST) | [5 empty] | 255130.6
11KV Line Material civil works
1 | SWR34179 | Hire-JCB to Level & Clear the Site | 2 | H | 2165 | 4330
2 | SWR33015 | Excavation in Ordinary Soil | 3.38 | M3 | 486 | 1642.68
3 | SWR33041 | CRS Masonary CM(1:6) 2nd Sort | 10.21 | M3 | 4925 | 50284.25
4 | SWR33403 | S&F MS Security Fencing Mesh (2"X2") | 10 | M2 | 2310 | 23100
5 | SWR34470 | Seigniorage Charges - Sand | 10.03 | M3 | 40 | 401.2
6 | SWR34471 | Seigniorage Charges - Metal | 5 | M3 | 97.5 | 487.5
7 | SWR34472 | Seigniorage Charges - Gravel | 24.24 | M3 | 30 | 727.2
8 | SWR10860 | Supply & Spreading of 20mm HBG metal | 5 | M3 | 2113 | 10565
9 | SWR33028 | PCC with 40mm Metal (1:4:8) | 1 | M3 | 4706 | 4706
10 | SWR33030 | PCC with 20mm Metal (1:2:4) | 0.25 | M3 | 6449 | 1612.25
11 | SWR33052 | S&Filling with Borrowed Gravel | 25.24 | M3 | 480 | 12115.2
Schedule Cost. (Excluding GST) | [5 empty] | 109971.28
|  | TOTAL Schedule Cost. (Excluding GST) | 580237.5
|  | GST@18% | 104442.75
|  | TOTAL Schedule Cost | 684680.25

## Metkhanguda feeder
Schedule (WBS No.T-2432-07-05-01-02-003)
Schedule for proposal for providing of 1280mtrs of new 11KV feeder from 33/11KV Suraram Ss with stringing of 1280mtrs of 11KV 3X185+70Sq.mm. AB cable over now proposed 9.1mtr PSCC poles and existing Poles duly tagging to existing 11KV IDLE VCB Breaker for bifurcation of 11KV Metkhanguda feeder emanating from 33/11KV Ushamullapudi SS in Gajularamaram Section of Quthbullapur Sub-Division of Medchal Division and the Work executed by the Construction Division of Medchal Circle under T&D Improvement to original Works Summer Action Plan-2024-2025 - Estimate Submitted - Reg.
Sl.No. | SSR CODES | Particulars | Qty | Rate in Rs. | Per Unit | Amount in Rs.
1 | SWR10393 | Erection of AB Switch and aligment complete Erection of 11KV 400/200A Conventional type AB Switch including fixing of cross angles and alignment complete | 2 | EA | 3200 | 6400
2 | SWR10881 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied Painting of operating rods of 33kV, 11kV AB switches with post office red colour (including cost of paint) | 2 | EA | 142 | 284
3 | SWR12331 | Making of coil earthing pole with 8mm GI wireNut&Bolts for AB Switch | 2 | EA | 146.63 | 293.26
4 | SMR40091 | Earthing of Sub-Station Supply of GI pipe 40 mm dia, 2 mtrs, 3mm thickness with bolts and nuts | 6 | EA | 733 | 4398
5 | SWR10357 | Providing of earthing with excavation of earth pit (0.6x0.6x2.4 Mts.) duly filling with bentonite, earth ,running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.6M dia x 0.5 M height . | 6 | EA | 1234.2 | 7405.2
6 | SWR10356 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand,Cement and curing etc.Including the cost of cement | 20.64 | M3 | 6579 | 135790.56
7 | SMR11488 | Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50 M height | 70 | KG | 117.5 | 8225
8 | SMR40133 | S-185Sqmm Alluminium Lug | 18 | EA | 13 | 234
9 | SWR10238 | LOADING of LINE MATERIALS 11 KV AB SWCH Con 200/400 A | 2 | EA | 80 | 160
10 | SWR10556 | UNLOADING of LINE MATERIALS 11 KV AB SWCH Con 200/400 A | 2 | EA | 80 | 160
11 | SWR10343 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports,back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation 9.1 M long PSCC pole | 30 | EA | 2400 | 72000
12 | SWR10107 | Excavation of pits in all soils except hard rock requiring blasting 0.76 M x 0.76M x 1.83M (2.6" x 2.6" x 6.0") 1.05 cum | 29 | EA | 700 | 20300
13 | SWR20308 | Sub-transport of poles upto Workspot upto 10KM (Including loading and unloading)9.1 Mtrs long PSCC Poles | 30 | EA | 407.29 | 12218.7
14 | SWR24971 | Supply and erection of T-Branch kit | 4 | EA | 3215 | 12860
15 | SMR11504 | S-of 11KV AB cable end kits | 18 | SET | 950 | 17100
16 | SWR10667 | End Termination of AB cable (each lead):120 Sqmm to 185 Sqmm | 18 | EA | 800 | 14400
17 | SWR10673 | Straight through joints of AB cable (each lead)Supply and ere Angle line Asmbly kits | 22 | EA | 2124 | 46728
18 | SMR12099 | Supply and Erection of I Hook and Suspension Hook Supply- I Hook | 62 | EA | 158 | 9796
19 | SWR12099 | Supply and Erection of I Hook and Suspension Hook Erection- I Hook | 62 | EA | 55 | 3410
20 | SWR10454 | Stringing of HT AB Cable with GI Metal Parts HT AB Cable 11 KV 3x185+70 Sqmm | 1.28 | KM | 41876.1 | 53601.41
21 | SWR10672 | Straight through joints of AB cable (each lead)Supply and ere Straight line Asmbly kits | 40 | EA | 1661 | 66440
22 | SMR11485 | Supply of earthing pipe with materials Supply of GI Flat 25X3 mm | 70 | KG | 105 | 7350
23 | SWR10917 | Labour for Fixing of all types of clamps | 40 | EA | 65 | 2600
24 | SWR11269 | Fixing of Side Arm along with Cross Arm including angle strut up to 5 feet 11KV | 7 | EA | 455 | 3185
25 | SWR10204 | LOADING of LINE MATERIALS R.S. Joists 175 x 85 mm | 10 | EA | 76 | 760
26 | SWR10522 | UNLOADING of LINE MATERIALS R.S. Joists 175 x 85 mm | 10 | EA | 50 | 500
27 | SWR10206 | LOADING of LINE MATERIALS MS hannel,Angles,Flats&Rods | 0.7 | TO | 221 | 154.7
28 | SWR10524 | UNLOADING of LINE MATERIALS MS Channel,Angles,Flats&Rod | 0.7 | TO | 185 | 129.5
29 | SWR12413 | LOADING of LINE MATERIALS 11 KV AB Cable (XLPE) 3 Core | 2 | DR | 584 | 1168
30 | SWR12431 | UNLOADING of LINE MATERIALS 11 KV AB Cable (XLPE) 3 Cor | 2 | DR | 438 | 876
31 | SWR11234 | LOADING of LINE MATERIALSUnwinding 11KV AB cable(3C/75mm LT) | 280 | M | 6 | 1680
32 | SWR11235 | UNLOADING of LINE MATERIALS Unwinding 11KV AB cabl(3C/75mm LT | 280 | M | 6 | 1680
33 | SWR11248 | LOADING of LINE MATERIALS 11KV Polymer Pin Insulator-GI pin | 27 | EA | 1 | 27
34 | SWR11249 | UNLOADING of LINE MATERIALS 11KV Polymer Pin Insulator-GI pin | 27 | EA | 1 | 27
35 | SWR10298 | Cutting charges for MS Sections RS Joists 175 x 85 mm | 10 | EA | 47 | 470
36 | SWR10294 | Cutting charges for MS Sections MS Channel 100 x 50 mm | 20 | EA | 10 | 200
37 | SWR10301 | Cutting charges for MS Sections MS flat of all sizes | 60 | EA | 2 | 120
38 | SWR10304 | Drilling of holes upto 20 mm dia using power drills RS Joists | 20 | EA | 12 | 240
39 | SWR10320 | Fabrication of materials including 2 coats of Red oxide painting Back clamps with 50 x 6 mm MS Flat | 60 | EA | 15 | 900
40 | SWR11263 | Fabrication of materials including 2 coats of Red oxide paintingStrut clamps with 50 x 6 mm MS Flat | 10 | SET | 50 | 500
41 | SWR10112 | Excavation of pits in hard rock requiring blasting. (other than SS)0.76 M x 0.76M x 1.83M (2.6" x 2.6" x 6.0") | 6 | EA | 1770 | 10620
42 | SWR11266 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports,back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation Box pole 9/10/11 Mtr | 5 | EA | 2643.83 | 13219.15
43 | SWR10671 | T' Branche Erection of Assemble Kit for 'T' Branche Kit | 4 | EA | 1800 | 7200
44 | SWR10640 | Painting of R.S Joist,Box poles including cross arms and clamps with one coat of red oxid and two coats of Al.paint including cost of paint and consumables | 5 | EA | 1132 | 5660
45 | SWR12125 | Providing of RCC collar to earth pit. Running of GI eartn flat of size 25X3mm from all metallic parts of channels, AB Switch, HG fuse set,DTr neutral and LT Distribution box and inter connection of earth pits etc complete | 70 | M | 14.03 | 982.1
46 | SMR25160 | S-Insulating Piercing Connector | 6 | EA | 1050 | 6300
47 | SWR25160 | Fix-Insulating Piercing Connector | 6 | EA | 300 | 1800
48 | SWR10653 | Formation of Cut point for 11 KV Single Circuit line excluding pole erection and stays | 4 | EA | 1435.81 | 5743.24
49 | SWR11862 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels,current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)Note: 1). It will be treated as full load of 10 MT and paid for 10 MT. 2). For 3 Ton vehicle : 50% of the following rates Above 20 Km and upto 30 Km with Lorry for each trip | 2 | EA | 3691.38 | 7382.76
50 | SWR11715 | Fabrication of poles 11KV Seating Channel | 4 | EA | 131 | 524
51 | SMR11486 | Supply of earthing pipe with materials Supply of GI wire No 8 | 6 | KG | 105 | 630
52 | SWR11715 | Fabrication of poles: 11KV Seating Channel | 4 | EA | 131 | 524
53 | SMR11486 | Supply of earthing pipe with materials Supply of GI wire No 8 | 6 | KG | 105 | 630
54 | SWR10214 | LOADING of LINE MATERIALS LT Pin insulators | 1 | BAG | 26 | 26
55 | SWR10532 | UNLOADING of LINE MATERIALS LT Pin insulators | 1 | BAG | 18 | 18
56 | SWR12400 | LOADING of LINE MATERIALS LTPins | 0.5 | BAG | 54 | 27
57 | SWR12420 | UNLOADING of LINE MATERIALS LTPins | 0.5 | BAG | 38 | 19
58 | SWR10642 | Fabrication of 175x85/150x75mm RS joist pieces upto 12.5 meters length by welding joint together by means of 50x6mm flat and MS channel on either side including the cost of consumable. | 5 | EA | 512.55 | 2562.75
59 | SWR11720 | 11KV side arm 75x40mm Channel 65x65x6mm Angle | 7 | EA | 100 | 700
Schedule Cost. (Excluding GST) | [5 empty] | 579339.33
GST@18% | [5 empty] | 104281.0794
Total Schedule Cost | [5 empty] | 683620.4094

## balaji hospital & pragatool
Schedule (WBS No.T-2432-07-05-01-02-008 & T-2432-07-05-01-02-007 )
Name of the work:Providing of 3500Mtrs of new 11KV feeder from 33/11KV Petbasheerabad SS with stringing of 3500Mtrs of 11KV 3X185+70Sqmm AB Cable over now proposed 9.1Mtr PSCC poles and existing poles along with erection of 1No.11KV Bay & breaker for bifurcation existing 11KV Balaji Hospital feeder emanating from 33/11KV Petbasheerabad SS and bifurcation of existing 11KV Pragatool feeder emanating from 33/11KV Subhash nagar SS by proposing 2.1KM of new 11KV feeder from the same SS with stringing of 0.6KM of 100Sqmm.AAA Conductor & 1.5KM of 11KV AB Cable (3x185+70Sq.mm) on 11Mts &9.1Mtr PSCC poles & laying of 150mtrs (DR) of 11KV XLPE 3x185Sqmm UG Cable duly erecting additional 1No.11KV Bay & Breaker at 33/11KV Subhash nagar SS in petbasheerabad section of Quthbullapur sub-division of Medchal Division of Medchal Circle (Reserved for SC).
Sl.No. | SSR CODES | Estimate Quantity (Only figures) | Particulars | Work Type eg., Earth Work, Electrical works..etc., (Upto 200 Characters) | Item Short Description | APSS/Morth CI.Number (Upto 200 characters) | Rate INR upto 2 Decimals | UOM (upto 50 Characters) | Amount INR (Upto 2 Decimals)
1 | SWR10461 | 2 | Erection of AB Switches, VCBs, LAs, PTs, CTs, DTRs etc Erection of 11 KV VCB with Control Panel | Erection work | Erection of work | As per relevent standard specification | 12000 | EA | 24000
2 | SMR11482 | 9 | Supply of earthing pipe with materials iii)Supply of CI earth pipe 100 mm dia, 2.75 mt long thickness 10mm with flange as per specication | Supply work | Supply of work | As per relevent standard specification | 3486 | EA | 31374
3 | SWR10356 | 24.54 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand,Cement and curing etc.Including the cost of cement | Erection work | Erection of work | As per relevent standard specification | 6579 | M3 | 161448.66
4 | SMR11488 | 300 | Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50 M height | Erection work | Erection of work | As per relevent standard specification | 117.5 | KG | 35250
5 | SWR10942 | 1 | Testing of Sub-Station Equipment Wirring, commissioning and testing of Outdoor Sub-station switchgear duly conducting the pre commissioning test as per relevent standards & issue of certificate by CEIG authorised testing Engineer | Erection work | Erection of work | As per relevent standard specification | 1825 | EA | 1825
6 | SWR12092 | 6 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders)(0.75M x 0.75M x 2.5M) 1.406 cum | Excavation work | Excavation of work | As per relevent standard specification | 1063.35 | EA | 6380.1
7 | SWR10238 | 8 | LOADING of LINE MATERIALS 11 KV AB SWCH Con 200/400 A | LOADING work | LOADING of work | As per relevent standard specification | 80 | EA | 640
8 | SMR40025 | 6 | Supply of clamps as per IS 5561- 1970 , 12mm thickness with Alluminum and Alluminum alloy Supply of Alluminum PT clamps conforming to A6 of IS 617, with hot dip galvanised bolts and nuts suitable for single zebra / Panther | Supply work | Supply of work | As per relevent standard specification | 368 | EA | 2208
9 | SMR40070 | 1 | Earth rods with (1) reputed make ISI PVC pipe of 5 feet length, 3 mm thickness, 32 mm dia inside cane wood stick closed both top & bottom ends with caps, (2) reputed make ISI (Finolex/ Polycab/Havells) first quality flexible PVC wire of 6 Sq.mm multi-strand copper 10 Mtrs length one side crimped with a suitable copper lug, other side fixed with a lug, bolt & nut to a suitable 3 inch long copper heavy duty crocodile clip having insulated sleeves, (3) Copper flat of size 25 mm width 3 mm thick 250 mm length make hook shape fixed to the PVC pipe with 2 No.s 6 mm dia 65 mm length hot dip galvanized bolts triple nuts with a 2 mm thick spring washer and 1 mm thick 4 flat washers and fixing of the copper wire to the bolts with lugs.Danger boards with clamps | Earthing work | Earthing of work | As per relevent standard specification | 116 | EA | 116
10 | SWR10917 | 33 | Labour for Fixing of all types of clamps | Erection work | Erection of work | As per relevent standard specification | 65 | EA | 2145
11 | SWR10393 | 7 | Erection of AB Switch and aligment complete Erection of 11KV 400/200A Conventional type AB Switch including fixing of cross angles and alignment complete | Erection work | Erection of work | As per relevent standard specification | 3200 | EA | 22400
12 | SWR11861 | 2 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels,current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading) Note: 1). It will be treated as full load of 10 MT and paid for 10 MT. 2). For 3 Ton vehicle : 50% of the following rates Above 10 Km and upto 20 Km with Lorry for each trip | Transport work | Transport of work | As per relevent standard specification | 3299.7 | EA | 6599.4
13 | SWR10199 | 2 | LOADING of LINE MATERIALS 11 KV VCBs&Panel boards | LOADING work | LOADING of work | As per relevent standard specification | 1024 | EA | 2048
14 | SWR10517 | 2 | UNLOADING of LINE MATERIALS 11 KV VCBs&Panel boards | UNLOADING work | UNLOADING of work | As per relevent standard specification | 1044.48 | EA | 2088.96
15 | SWR10556 | 6 | UNLOADING of LINE MATERIALS 11 KV AB SWCH Con 200/400 A | UNLOADING work | UNLOADING of work | As per relevent standard specification | 80 | EA | 480
16 | SWR11266 | 14 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports,back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation Box pole 9/10/11 Mtr | Erection work | Erection of work | As per relevent standard specification | 2643.83 | EA | 37013.62
17 | SWR10204 | 12 | LOADING of LINE MATERIAL SR.S. Joists 175 x 85 mm | LOADING work | LOADING of work | As per relevent standard specification | 76 | EA | 912
18 | SWR10522 | 12 | UNLOADING of LINE MATERIALS R.S. Joists 175 x 85 mm | UNLOADING work | UNLOADING of work | As per relevent standard specification | 50 | EA | 600
19 | SWR10206 | 7.52 | LOADING of LINE MATERIALS MS Channel,Angles,Flats&Rods | LOADING work | LOADING of work | As per relevent standard specification | 221 | TO | 1661.92
20 | SWR10524 | 7.52 | UNLOADING of LINE MATERIALS MS Channel,Angles,Flats&Rod | UNLOADING work | UNLOADING of work | As per relevent standard specification | 185 | TO | 1391.2
21 | SWR10265 | 3 | LOADING of LINE MATERIALS 11 KV, 10 KA LAs Line type | LOADING work | LOADING of work | As per relevent standard specification | 32 | EA | 96
22 | SWR10583 | 3 | UNLOADING of LINE MATERIALS 11 KV, 10 KA LAs Line type | UNLOADING work | UNLOADING of work | As per relevent standard specification | 32 | EA | 96
23 | SWR11701 | 270 | LOADING of LINE MATERIALS PVC Control Cable 10C | LOADING work | LOADING of work | As per relevent standard specification | 1 | M | 270
24 | SWR11712 | 270 | UNLOADING of LINE MATERIALS PVC Control Cable 10C | UNLOADING work | UNLOADING of work | As per relevent standard specification | 1.02 | M | 275.4
25 | SWR10298 | 24 | Cutting charges for MS Sections RS Joists 175 x 85 mm | Civil work | Civil of work | As per relevent standard specification | 47 | EA | 1128
26 | SWR10307 | 120 | Drilling of holes upto 20 mm dia using power drills MS Channel, Angles and flat | Civil work | Civil of work | As per relevent standard specification | 4 | EA | 480
27 | SWR10359 | 10 | Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50 M height | Earthing work | Earthing of work | As per relevent standard specification | 386 | EA | 3860
28 | SWR12294 | 0.52 | Excavatin of pit Providing of Base Concreting (Pole pits- 076 M x 0.76M x 0.15M ) with 1:3:6 Concrete Mix including curing with water | Excavatin work | Excavatin of work | As per relevent standard specification | 5053 | M3 | 2627.56
29 | SWR10868 | 1.5 | Fabrication of Main and Auxiliary structures with power drilling using raw steel such as M.S.Angles, Plates, Channels, R.S.Joists, including the supply and fabrication of 6mm base and top plate for Box pole to the RSJoist poles excluding cost of Mild Steel and transport charges to substation site, including erection. | Fabrication work | Fabrication of work | As per relevent standard specification | 6852 | TO | 10278
30 | SWR10867 | 1.5 | Alligning the Main and Auxiliary structures such as RS joist, M.S.Angles, Plates, Channels, Structure to zero level duly leveling in prefabricated MS frames with Hydraulic jacks before galvanising/ fabrication. | Civil work | Civil of work | As per relevent standard specification | 1470 | TO | 2205
31 | SWR21241 | 2 | Hoisting of Insulators and hardware, stretching the conductor and stringing of 11 kV bus comprising of three phases with Single Zebra/panther conductor to a tension of 450kgs.(Bus section of 3.5mt) | Civil work | Civil of work | As per relevent standard specification | 507 | EA | 1014
32 | SMR11915 | 6 | Supply of Tension Hardware 3 Bolted for single Zebra/panther with 150 mm spacing. | Supply work | Supply of work | As per relevent standard specification | 2055 | SET | 12330
33 | SWR11890 | 0.186 | Mass Concreting for pole Coping of 1.5'x1.5'x1 with 1:8 slope Using form boxes (0.031Cumt.) | Mass Concreting work | Mass Concreting of work | As per relevent standard specification | 3893.01 | M3 | 724.0999
34 | SMR40011 | 18 | Supply of clamps as per IS 5561- 1970 , 12mm thickness with Alluminum and Alluminum alloy Supply of Alluminum alloy T clamps conforming to A6 of IS 617, 4 bolted with hot dip galvanised bolts and double nuts with spring and flat washers of size M10 x 65 i.e(3/8" x 21/2 " to suit for panther ACSR on all three ways /on one side and Zebra ACSR on take off side or any other combination for carrying 800 A current rating | Supply work | Supply of work | As per relevent standard specification | 299 | EA | 5382
35 | SMR22473 | 3 | Supply of clamps as per IS 5561- 1970 , 12mm thickness with Alluminum and Alluminum alloy Supply of I Bolts | Supply work | Supply of work | As per relevent standard specification | 294 | EA | 882
36 | SMR40009 | 2.2 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1stgrade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied Supply of material cost for First coat of 1st Grade Aluminium Paint,brushes etc. | Civil work | Civil of work | As per relevent standard specification | 2181 | TO | 4798.2
37 | SWR10877 | 2.2 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1stgrade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied Labour charges for painting including scratching and cleaning of Substationstructures of 1st coat of Aluminium | Civil work | Civil of work | As per relevent standard specification | 851 | TO | 1872.2
38 | SMR40010 | 2.2 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1stgrade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied (*)Supply of material cost for Second coat of 1st Grade Aluminium Paint brushes, etc. | Civil work | Civil of work | As per relevent standard specification | 1293 | TO | 2844.6
39 | SWR10879 | 2.2 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1stgrade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied Labour charges for painting including scratching and cleaning of Substation structures of 2nd coat of Aluminium . | Civil work | Civil of work | As per relevent standard specification | 482 | TO | 1060.4
40 | SWR10920 | 103.83 | Laying of earth mat including excavation of trenches of depth 600mm, welding, connecting to equipment and connecting lightning shield to earth mat and earthing of fence posts, drilling and connecting earth rods including connecting cast iron pipes with the following sizes of MS Flats /GI Flats. including fabrication.75x 8mm MS Flat / GI Flat. | Earthing work | Earthing of work | As per relevent standard specification | 65 | RMT | 6748.95
41 | SWR10919 | 50 | Fabrication and connecting to risers from earth mat to structures, equipment,marshalling boxes, electrical panels, PLCC panels, fencing posts etc.M.S./ G.I. Flat 50x6mm / 50 x 8 mm ( Above ground) | Fabrication work | Fabrication of work | As per relevent standard specification | 41 | RMT | 2050
42 | SWR12510 | 100 | L-Cable Termination to Switchgear | Civil work | Civil of work | As per relevent standard specification | 27 | EA | 2700
43 | SWR11089 | 10 | Painting of poles Paint of coping with 2 coats of white cement incl cost of paints etc. | Civil work | Civil of work | As per relevent standard specification | 48 | EA | 480
44 | SWR12331 | 8 | Making of coil earthing pole with 8mm GI wireNut&Bolts for AB Switch | Earthing work | Earthing of work | As per relevent standard specification | 146.63 | EA | 1173.04
45 | SWR10881 | 8 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied Painting of operating rods of 33kV, 11kV AB switches with post office red colour (including cost of paint) | Civil work | Civil of work | As per relevent standard specification | 142 | EA | 1136
46 | SWR10860 | 5.5 | Supply & spreading of 20mm machine crushed metal (HBG) including cost of conveneyance of all materials, labour charges etc complete for finished item of work and directed by the engineer incharge | Supply work | Supply of work | As per relevent standard specification | 2113 | M3 | 11621.5
47 | SWR10743 | 8 | Providing of earthing with excavation of earth pit (0.6x0.6x2.4 Mts.) duly filling with bentonite, earth ,running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.6M dia x 0.5 M height . | Earthing work | Earthing of work | As per relevent standard specification | 686 | EA | 5488
48 | SWR10357 | 17 | Supply of earthing pipe with materials. Supply of GI Flat 25X3 mm | Supply work | Supply of work | As per relevent standard specification | 1234.2 | EA | 20981.4
49 | SMR11485 | 125 | Supply of earthing pipe with materials Supply of GI Flat 25X3 mm | Supply work | Supply of work | As per relevent standard specification | 105 | KG | 13125
50 | SWR10732 | 2 | Con of Plinth for 11kv VCB 1.8x1.8x0.75m | Civil work | Civil of work | As per relevent standard specification | 27629 | EA | 55258
51 | SWR11973 | 95 | Laying of XLPE UG cable Double Run including excavation of trench of size 600mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV from road level and cable separation with machine cut bricks horizontally for every 3meters , providing of DWC/GI pipes wherever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth,levelling and removing the debris from the site inluding the cost of lead and lift etc.. (Second cable laying cost not Included) depth of the trench LT-0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs.In Hard Gravel Soil / BC soil / Red earth / stone and earth mixed with fair boulders / Normal soil/CC 11 KV 3x300 Sqmm Cable | Excavatin work | Excavatin of work | As per relevent standard specification | 631.06 | M | 59950.7
52 | SWR12005 | 25 | Raising of double run cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe)11 KV 3x300 Sqmm Cable | 15 | Erection of work | As per relevent standard specification | 275.4 | M | 6885
53 | SWR10391 | 8 | Making of Outdoor/Indoor End Termination 11 KV 3x300 Sqmm Cable | Erection work | Erection of work | As per relevent standard specification | 2370.63 | EA | 18965.04
54 | SWR20863 | 4 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports,back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation | Erection work | Erection of work | As per relevent standard specification | 1044.23 | EA | 4176.92
55 | SWR10298 | 6 | Cutting charges for MS Sections RS Joists 175 x 85 mm | Erection work | Erection of work | As per relevent standard specification | 47 | EA | 282
56 | SWR21277 | 2 | Erection of 11KV 800A double throw AB Switches | Erection work | Erection of work | As per relevent standard specification | 3500 | EA | 7000
57 | SWR20768 | 7.78 | Earth work excavation of in all soils except hard rock requiring blasting. | Earthing work | Earthing of work | As per relevent standard specification | 345 | M3 | 2684.1
58 | SWR10108 | 6 | Excavation of pits in all soils except hard rock requiring blasting 0.75 M x 0.9 M x 1.95 M (1.31 cum) | Excavatin work | Excavatin of work | As per relevent standard specification | 629.85 | EA | 3779.1
59 | SWR11879 | 300 | Laying of 4 core/10 core 2.5 sq. mm.Copper control cable in aready excavation trench including cost of providing single compress glands at both ends . | Erection work | Erection of work | As per relevent standard specification | 27 | M | 8100
60 | SWR10869 | 1.12 | Fabrication of Main and Auxiliary structures with welding using raw steel such as RS joist, M.S.Angles, Plates, Channels, including the supply and fabrication of 6mm base plate to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection. | Fabrication work | Fabrication of work | As per relevent standard specification | 3426 | TO | 3837.12
61 | SWR11891 | 15 | Laying of earth mat including excavation of trenches of depth 600mm,welding, connecting to equipment and connecting lightning shield to earth mat and earthing of fence posts, drilling and connecting earth rods including connecting cast iron pipes with the following sizes of MS Flats /GI Flats. including fabrication.Connecting with GI Wire No.8 (Labour) | Earthing work | Earthing of work | As per relevent standard specification | 14 | M | 210
62 | SWR10205 | 6 | LOADING of LINE MATERIALS RSJoists150 x 150 mm/RailPole | LOADING work | LOADING of work | As per relevent standard specification | 176 | EA | 1056
63 | SWR10523 | 6 | UNLOADING of LINE MATERIALS RSJoists150 x150 mm/RailPol | UNLOADING work | UNLOADING of work | As per relevent standard specification | 107 | EA | 642
64 | SWR23105 | 550 | LOADING of LINE MATERIALS PVC Control Cb 4, 10C | LOADING work | LOADING of work | As per relevent standard specification | 1 | M | 550
65 | SWR23106 | 550 | UNLOADING of LINE MATERIALS PVC Control Cb 4, 10C | UNLOADING work | UNLOADING of work | As per relevent standard specification | 0.15 | M | 82.5
66 | SWR10988 | 40 | Laying of the cable along the footpath through 225mm dia GI pipe for 33KV, 150mm dia GI pipe for 11KV (excluding the cost of GI pipe)Laying of 2nd cable in excavated trench | Earthing work | Earthing of work | As per relevent standard specification | 204.1 | M | 8164
67 | SWR10884 | 2 | Connection of equipment to bus and or another equipment with single zebra/Panther conductor including measuring, cutting,clamping and hoisting of suspension insulator assembly to support the conductor wherever necessary. | Earthing work | Earthing of work | As per relevent standard specification | 224 | EA | 448
68 | SWR10398 | 1 | Erection of AB Switches, VCBs, LAs, PTs, CTs, DTRs etc Erection of 11 KV LAS line type including earthing | Erection work | Erection of work | As per relevent standard specification | 505 | SET | 505
69 | SWR11040 | 9 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders) 0.75 M x 0.9 M x 1.95 M | Excavatin work | Excavatin of work | As per relevent standard specification | 990.68 | EA | 8916.12
70 | SWR10133 | 2.92 | Transport of iron materials such as R.S. Joists, Rail Poles, fabricated supports, steel, iron, flat, M.S.Channels etc., by lorries. (excluding of loading & unloading )Above 20 KM and upto 30 KM | Transport work | Transport of work | As per relevent standard specification | 476.34 | TO | 1390.9128
71 | SWR11862 | 5 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels,current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading) Note: 1). It will be treated as full load of 10 MT and paid for 10 MT. 2). For 3 Ton vehicle : 50% of the following rates Above 20 Km and upto 30 Km with Lorry for each trip | Transport work | Transport of work | As per relevent standard specification | 3691.38 | EA | 18456.9
72 | SWR11873 | 25 | Cutting charges for MS Sections MS Channel 75 x 40 mm | Civil work | Civil of work | As per relevent standard specification | 9 | EA | 225
73 | SWR11180 | 3 | Sub-transport of poles upto Workspot upto 10KM (Including loading and unloading)11 Mtrs long PSCC Poles | Sub-transport work | Sub-transport of work | As per relevent standard specification | 431.97 | EA | 1295.91
74 | SWR34252 | 50 | S&R 25x6mm GI Strip for Earthing | Earthing work | Earthing of work | As per relevent standard specification | 113 | M | 5650
75 | SWR10978 | 3 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports,back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation 11 Mtrs PSCC poles | Erection work | Erection of work | As per relevent standard specification | 4336.85 | EA | 13010.55
76 | SWR20308 | 59 | Sub-transport of poles upto Workspot upto 10KM (Including loading and unloading)9.1 Mtrs long PSCC Poles | Sub-transport work | Sub-transport of work | As per relevent standard specification | 407.29 | EA | 24030.11
77 | SWR23200 | 1000 | Cut-Tree Branch(LT/11/33)&Trnsprt Debris | Civil work | Civil of work | As per relevent standard specification | 4 | EA | 4000
78 | SWR10107 | 59 | Excavation of pits in all soils except hard rock requiring blasting 0.76 M x 0.76M x 1.83M (2.6" x 2.6" x 6.0") 1.05 cum | Excavatin work | Excavatin of work | As per relevent standard specification | 700 | EA | 41300
79 | SWR11974 | 130 | Laying of XLPE UG cable Double Run including excavation of trench of size 600mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV from road level and cable separation with machine cut bricks horizontally for every 3meters , providing of DWC/GI pipes wherever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth,levelling and removing the debris from the site inluding the cost of lead and lift etc.. (Second cable laying cost not Included) depth of the trench LT-0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs.In Hard Gravel Soil / BC soil / Red earth / stone and earth mixed with fair boulders / Normal soil/CC 11 KV 3x185 Sqmm Cable | Excavatin work | Excavatin of work | As per relevent standard specification | 631.06 | M | 82037.8
80 | SWR12006 | 20 | Raising of double run cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe)11 KV 3x185 Sqmm Cable | Erection work | Erection of work | As per relevent standard specification | 243.53 | M | 4870.6
81 | SWR10390 | 4 | Making of Outdoor/Indoor End Termination 11 KV 3x185 Sqmm Cable | Erection work | Erection of work | As per relevent standard specification | 2370.63 | EA | 9482.52
82 | SWR11308 | 0.32 | Restringing of existing loose Lines by removing the pin-binding and jumpers,Providing of temporary stays, providing stiffners pieces, replacement of damaged insulators, alignment of cross arms, pin binding and jumpering after tensioning and removing of the temporary stays complete-Restringing of with 55 Sqmm single ckt 3 cond | Civil work | Civil of work | As per relevent standard specification | 6616 | KM | 2117.12
83 | SWR10642 | 8 | Fabrication of 175x85/150x75mm RS joist pieces upto 12.5 meters length by welding joint together by means of 50x6mm flat and MS channel on either side including the cost of consumable. | Fabrication work | Fabrication of work | As per relevent standard specification | 512.55 | EA | 4100.4
84 | SWR10366 | 0.6 | Paving out and stringing of conductor by providing temporary stays, tensioning, sagging correctly, fixing strain points, transferring to pin points binding, keeping stifner, rectification of poles, guys and jumpering etc., including transport of material from road side to location.100 Sqmm Single Circuit (3 Conductors) | Erection work | Erection of work | As per relevent standard specification | 13856.7 | KM | 8314.02
85 | SWR10673 | 30 | Straight through joints of AB cable (each lead)Supply and ere Angle line Asmbly kits | Erection work | Erection of work | As per relevent standard specification | 2124 | EA | 63720
86 | SWR10672 | 148 | Straight through joints of AB cable (each lead)Supply and ere Straight line Asmbly kits | Erection work | Erection of work | As per relevent standard specification | 1661 | EA | 245828
87 | SMR12099 | 163 | Supply and Erection of I Hook and Suspension Hook Supply- I Hook | Supply work | Supply of work | As per relevent standard specification | 158 | EA | 25754
88 | SWR12099 | 163 | Supply and Erection of I Hook and Suspension Hook Erection- I Hook | Supply work | Supply of work | As per relevent standard specification | 55 | EA | 8965
89 | SWR12413 | 10 | LOADING of LINE MATERIAL 11 KV AB Cable (XLPE) 3 Core | LOADING work | LOADING of work | As per relevent standard specification | 584 | DR | 5840
90 | SWR12431 | 10 | UNLOADING of LINE MATERIAL 11 KV AB Cable (XLPE) 3 Cor | UNLOADING work | UNLOADING of work | As per relevent standard specification | 438 | DR | 4380
91 | SWR11248 | 213 | LOADING of LINE MATERIAL 11KV Polymer Pin Insulator-GI pin | LOADING work | LOADING of work | As per relevent standard specification | 1 | EA | 213
92 | SWR11249 | 213 | UNLOADING of LINE MATERIAL 11KV Polymer Pin Insulator-GI pin | UNLOADING work | UNLOADING of work | As per relevent standard specification | 1 | EA | 213
93 | SWR10320 | 140 | Fabrication of materials including 2 coats of Red oxide painting Back clamps with 50 x 6 mm MS Flat | Fabrication work | Fabrication of work | As per relevent standard specification | 15 | EA | 2100
94 | SWR11720 | 72 | 11KV side arm 75x40mm Channel 65x65x6mm Angle | Erection work | Erection of work | As per relevent standard specification | 100 | EA | 7200
95 | SWR11269 | 72 | Fixing of Side Arm along with Cross Arm including angle strut up to 5 feet 11KV | Erection work | Erection of work | As per relevent standard specification | 455 | EA | 32760
96 | SWR10671 | 11 | T' Branch Erection of Assemble Kit for 'T' Branche | Erection work | Erection of work | As per relevent standard specification | 1800 | EA | 19800
97 | SWR24971 | 11 | T-Branch kit Supply and erection of T-Branch kit | Erection work | Erection of work | As per relevent standard specification | 3215 | EA | 35365
98 | SMR11504 | 45 | End Termination of AB cable (each lead):Supply of 11KV 3x185+70sq.mm/3x70+70sq.mm/3x35+35sq.mm AB cable end Kits | Erection work | Erection of work | As per relevent standard specification | 950 | SET | 42750
99 | SWR10667 | 45 | End Termination of AB cable (each lead):120 Sqmm to 185 Sqmm | Erection work | Erection of work | As per relevent standard specification | 800 | EA | 36000
100 | SWR10204 | 4 | LOADING of LINE MATERIAL R.S. Joists 175 x 85 mm | LOADING work | LOADING of work | As per relevent standard specification | 76 | EA | 304
101 | SWR10522 | 4 | UNLOADING of LINE MATERIAL R.S. Joists 175 x 85 mm | UNLOADING work | UNLOADING of work | As per relevent standard specification | 50 | EA | 200
102 | SWR10640 | 4 | Painting of R.S Joist,Box poles including cross arms and clamps with one coat of red oxid and two coats of Al.paint including cost of paint and consumables | Civil work | Civil of work | As per relevent standard specification | 1132 | EA | 4528
103 | SMR11486 | 43 | Supply of earthing pipe with materials,GI wire No 8 | Supply work | Supply of work | As per relevent standard specification | 105 | KG | 4515
104 | SMR40091 | 11 | Earthing of Sub-Station Supply of GI pipe 40 mm dia, 2 mtrs, 3mm thickness with bolts and nuts | Earthing work | Earthing of work | As per relevent standard specification | 733 | EA | 8063
105 | SWR10343 | 59 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports,back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation 9.1 M long PSCC pole | Erection work | Erection of work | As per relevent standard specification | 2400 | EA | 141600
106 | SMR40133 | 27 | S-185Sqmm Alluminium Lug | Supply work | Supply of work | As per relevent standard specification | 13 | EA | 351
107 | SWR10319 | 40 | Fabrication of materials including 2 coats of Red oxide painting Back clamps with 75 x 8 mm MS Flat | Fabrication work | Fabrication of work | As per relevent standard specification | 31 | EA | 1240
108 | SWR10454 | 3.5 | Stringing of HT AB Cable with GI Metal Parts HT AB Cable 11 KV 3x185+70 Sqmm | Erection work | Erection of work | As per relevent standard specification | 41876.1 | KM | 146566.35
109 | SWR10294 | 25 | Cutting charges for MS Sections MS Channel 100 x 50 mm | Erection work | Erection of work | As per relevent standard specification | 10 | EA | 250
110 | SWR10301 | 30 | Cutting charges for MS Sections MS flat of all sizes | Erection work | Erection of work | As per relevent standard specification | 2 | EA | 60
111 | SWR21914 | 7 | Erection of Insulated Connectors with covers | Erection work | Erection of work | As per relevent standard specification | 80 | EA | 560
112 | SMR25160 | 7 | S-Insulating Piercing Connector | Supply work | Supply of work | As per relevent standard specification | 1050 | EA | 7350
113 | SWR12125 | 70 | Providing of RCC collar to earth pit.Running of GI eartn flat of size 25X3mm from all metallic parts of channels, AB Switch, HG fuse set,DTr neutral and LT Distribution box and inter connection of earth pits etc complete | Erection work | Erection of work | As per relevent standard specification | 14.03 | M | 982.1
114 | SWR11319 | 10 | Dismantling of Damaged Poles, not required and available in the middle of roads, transporting to stock point etc.Dism of 8.0M PSCC Pole | Dismantling work | Dismantling of work | As per relevent standard specification | 501.53 | EA | 5015.3
115 | SWR10109 | 6 | Excavation of pits in all soils except hard rock requiring blasting 0.92 M x 0.92M x 2.3M (3.0" x 3.0" x 7.6") 1.94 cum | Excavatin work | Excavatin of work | As per relevent standard specification | 842.78 | EA | 5056.68
116 | SWR10105 | 14 | Excavation of pits in all soils except hard rock requiring blasting 0.76 M x 0.76M x 1.52M (2.6" x 2.6" x 5.0') 0.88 cum | Excavatin work | Excavatin of work | As per relevent standard specification | 650 | EA | 9100
117 | SWR20307 | 14 | Sub-transport of poles upto Workspot upto 10KM (Including loading and unloading)8 Mtrs long PSCC Poles | Erection work | Erection of work | As per relevent standard specification | 271.52 | EA | 3801.28
118 | SWR10342 | 14 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports,back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation-Erection of 8M Pole | Erection work | Erection of work | As per relevent standard specification | 1500 | EA | 21000
119 | SWR10343 | 6 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports,back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation-Erection of 9.1M Pole | Erection work | Erection of work | As per relevent standard specification | 2400 | EA | 14400
120 | SWR34179 | 2 | Hire-JCB to Level & Clear the Site | Civil work | Civil work | As per relevent standard specification | 2165 | H | 4330
121 | SWR33015 | 7.78 | Excavation in Ordinary Soil | Civil work | Civil work | As per relevent standard specification | 486 | M3 | 3781.08
122 | SWR33041 | 28.51 | CRS Masonary CM(1:6) 2nd Sort | Civil work | Civil work | As per relevent standard specification | 4925 | M3 | 140411.75
123 | SWR33403 | 24 | S&F MS Security Fencing Mesh (2"X2") | Civil work | Civil work | As per relevent standard specification | 2310 | M2 | 55440
124 | SWR34470 | 10.03 | Seigniorage Charges - Sand | Civil work | Civil work | As per relevent standard specification | 40 | M3 | 401.2
125 | SWR34471 | 39.09 | Seigniorage Charges - Metal | Civil work | Civil work | As per relevent standard specification | 97.5 | M3 | 3811.275
126 | SWR34472 | 50 | Seigniorage Charges - Gravel | Civil work | Civil work | As per relevent standard specification | 30 | M3 | 1500
Schedule Cost. (Excluding GST) | [8 empty] | 1985588.6677