## Bowrampet Village Feeder
Schedule (WBS No.T-2432-07-05-01-03-001 and T-24321-07-05-01-03-003)
Name of the work: Bifurcation existing 11KV Bowrampet Village Feeder emanating from 33/11KV Bowrampet SS by stringing of 1.58 KM 11KV3x185sq.mm AB cable on Existing 9.1 Mtrs. PSCC Poles from 33/11KV Bowrampet SS to Bodrai Bowrampet and bifurcation existing 11KV CocaCola Feeder emanating from 33/11KV Bowrampet SS by laying of 0.52 KM of 11KV 3X185 AB CABLE and Stringing of AAA 55 Sq.mm Conductor for 2KM and 100 Sq.mm AAA Conductor for a lenght of 330 Mtrs on Existing 9.1 Mtrs. PSCC Poles from 33/11KV Bowrampet SS to Ullas Dhaba in Bowrampet Section of Jeedimetla Sub-Division in Jeedimetla Division in Medchal Circle under T&D Improvements to original Works- Summer action plan 2024-25 - Reg.
Sl.No. | SSR CODES | Estimate Quantity (Only figures) | Particulars | Work Type eg., Earth Work, Electrical works..etc., (Upto 200 Characters) | Item Short Description | APSS/Morth CI.Number (Upto 200 characters) | Rate INR upto 2 Decimals | UOM (upto 50 Characters) | UOM (upto 50 Characters) | Amount INR (Upto 2 Decimals)
1 | SWR10461 | 2 | Erection of AB Switches, VCBs, LAs, PTs, CTs, DTRs etc Erection of 11 KV VCB with Control Panel | Erection work | Erection of work | As per relevent standard specification | 12000 | EA | 12000 | 24000
2 | SMR11482 | 6 | Supply of earthing pipe with materials Supply of CI earth pipe 100 mm dia, 2.75 mt long thickness 10mm with flange as per specication | Supply work | Supply of work | As per relevent standard specification | 3486 | EA | 3486 | 20916
3 | SWR10356 | 13.6 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc.Mass concreting of supports incl. cement | Erection work | Erection of work | As per relevent standard specification | 6579 | M3 | 6579 | 89474.4
4 | SWR11879 | 1300 | Control Cable Laying of 4 core/10 core 2.5 sq. mm.Copper control cable in aready excavation trench including cost of providing single compress glands at both ends . | Earthing work | Earthing of work | As per relevent standard specification | 27 | M | 27 | 35100
5 | SMR11488 | 200 | Supply of earthing pipe with materials S-GI Bolts & Nuts,Washers etc., | Supply work | Supply of work | As per relevent standard specification | 117.5 | KG | 117.5 | 23500
6 | SWR10942 | 2 | Testing of Sub-Station Equipment Wirring, commissioning and testing of Outdoor Sub-station switchgear duly conducting the pre commissioning test as per relevent standards & issue of certificate by CEIG authorised testing Engineer | Electrical work | Erection of work | As per relevent standard specification | 1825 | EA | 1825 | 3650
7 | SWR12092 | 6 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders) (0.75M x 0.75M x 2.5M) 1.406 cum | Excavation work | Excavation of work | As per relevent standard specification | 1063.35 | EA | 1063.35 | 6380.1
8 | SWR10238 | 4 | Loading and Unloading Loading of 11KV AB Switch Conventional type | Erection work | Erection of work | As per relevent standard specification | 80 | EA | 80 | 320
9 | SMR40025 | 12 | Supply of clamps as per IS 5561- 1970 , 12mm thickness with Alluminum and Alluminum alloy conforming to A6 of IS 617 1994 & hot dip galvanised with Nuts & Bolts including spring washers conforming to IS 2633-1964, IS 1363-1967, IS1367- 1961) Sup PT clamps for single zebra / Panther | Supply work | Supply of work | As per relevent standard specification | 368 | EA | 368 | 4416
10 | SMR40070 | 2 | Danger boards with clamps | Electrical work | Erection of work | As per relevent standard specification | 116 | EA | 116 | 232
11 | SWR10917 | 30 | Labour for Fixing of all types of clamps | Electrical work | Erection of work | As per relevent standard specification | 65 | EA | 65 | 1950
12 | SWR10393 | 4 | Erection of AB Switch and aligment complete Erection of 11KV 400/200A Conventional type AB Switch including fixing of cross angles and alignment complete | Erection work | Erection of work | As per relevent standard specification | 3200 | EA | 3200 | 12800
13 | SWR11861 | 4 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading) Above 10 Km and upto 20 Km with Lorry for each trip | Erection work | Erection of work | As per relevent standard specification | 3299.7 | EA | 3299.7 | 13198.8
14 | SWR10199 | 2 | Loading and Unloading Loading of 11 KV VCBs along with Panel boards | Erection work | Erection of work | As per relevent standard specification | 1024 | EA | 1024 | 2048
15 | SWR10517 | 2 | Loading and Unloading Un loading of 11 KV VCBs along with Panel boards | Erection work | Erection of work | As per relevent standard specification | 1044.48 | EA | 1044.48 | 2088.96
16 | SWR10556 | 4 | Un loading of 11KV AB Switch Conventional type | Erection work | Erection of work | As per relevent standard specification | 80 | EA | 80 | 320
17 | SWR11037 | 4 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders) 0.76 M x 0.76M x 1.52M (2.6" x 2.6" x 5.0') 0.88 cum | Electrical work | Erection of work | As per relevent standard specification | 793 | EA | 793 | 3172
18 | SWR10348 | 6 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation R.S. Joists 150 x 150 mm | Erection work | Erection of work | As per relevent standard specification | 1952.61 | EA | 1952.61 | 11715.66
19 | SMR11482 | 6 | Supply of earthing pipe with materials Supply of CI earth pipe 100 mm dia, 2.75 mt long thickness 10mm with flange as per specication | Supply work | Supply of work | As per relevent standard specification | 3486 | EA | 3486 | 20916
20 | SWR10205 | 6 | Loading and Unloading Loading of R.S. Joists 150 x 150mm / Rail poles | Erection work | Erection of work | As per relevent standard specification | 176 | EA | 176 | 1056
21 | SWR10523 | 6 | Loading and Unloading Un loading of R.S. Joists 150 x 150mm / Rail poles | Erection work | Erection of work | As per relevent standard specification | 107 | EA | 107 | 642
22 | SWR10206 | 3 | Loading and Unloading Loading of M.S.Channels, Angles, Flats & Rods etc., | Erection work | Erection of work | As per relevent standard specification | 221 | TO | 221 | 663
23 | SWR10524 | 3 | Loading and Unloading Un loading of M.S.Channels, Angles, Flats & Rods etc., | Erection work | Erection of work | As per relevent standard specification | 185 | TO | 185 | 555
24 | SWR10265 | 6 | Loading and Unloading Loading of 11 KV, 10 KA LAs Line type | Erection work | Erection of work | As per relevent standard specification | 32 | EA | 32 | 192
25 | SWR10583 | 6 | Loading and Unloading Un loading of 11 KV, 10 KA LAs Line type | Erection work | Erection of work | As per relevent standard specification | 32 | EA | 32 | 192
26 | SWR11701 | 1300 | Loading and Unloading Loading of PVC Control Cable 10 Core | Erection work | Erection of work | As per relevent standard specification | 1 | M | 1 | 1300
27 | SWR11712 | 1300 | Loading and Unloading Un loading of PVC Control Cable 10 Core | Erection work | Erection of work | As per relevent standard specification | 1.02 | M | 1.02 | 1326
28 | SWR11220 | 120 | Loading and Unloading Loading of Unwinding of panther conductor from main drum and recoiling | Erection work | Erection of work | As per relevent standard specification | 3 | M | 3 | 360
29 | SWR11221 | 120 | Loading and Unloading Un loading of Unwinding of panther conductor from main drum and recoiling | Erection work | Erection of work | As per relevent standard specification | 2 | M | 2 | 240
30 | SWR10297 | 6 | FABRICATION OF MATERIALS RS Joists 150 x 150 mm | FABRICATION work | FABRICATION of work | As per relevent standard specification | 48 | EA | 48 | 288
31 | SWR10307 | 240 | Drilling of holes upto 20 mm dia using power drills MS Channel, Angles and flat | FABRICATION work | FABRICATION of work | As per relevent standard specification | 4 | EA | 4 | 960
32 | SWR10359 | 6 | Providing of RCC collar to earth pit. Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50 M height | Civil work | Civil of work | As per relevent standard specification | 386 | EA | 386 | 2316
33 | SWR12294 | 0.5 | Excavatin of pit "Providing of Base Concreting with 1:3:6 Concrete Mix including materials & curing with water | Erection work | Erection of work | As per relevent standard specification | 5053 | M3 | 5053 | 2526.5
34 | SWR10868 | 3 | Fabrication & erection of Channels Fabrication of Main and Auxiliary structures with power drilling using raw steel such as M.S.Angles, Plates, Channels, R.S.Joists, including the supply and fabrication of 6mm base and top plate for Box pole to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection. | Electrical work | Erection of work | As per relevent standard specification | 6852 | TO | 6852 | 20556
35 | SWR10867 | 3 | Fabrication & erection of Channels Alligning the Main and Auxiliary structures such as RS joist, M.S.Angles, Plates, Channels, Structure to zero level duly leveling in prefabricated MS frames with Hydraulic jacks before galvanising/ fabrication. | Electrical work | Erection of work | As per relevent standard specification | 1470 | TO | 1470 | 4410
36 | SWR21241 | 2 | Bus Stringing Hoisting of Insulators and hardware, stretching the conductor and stringing of 11 kV bus comprising of three phases with Single Zebra/panther conductor to a tension of 450kgs.(Bus section of 3.5mt) | Electrical work | Erection of work | As per relevent standard specification | 507 | EA | 507 | 1014
37 | SMR11915 | 12 | Supply of Tension Hardware 3 Bolted for single Zebra/panther with 150 mm spacing. | Supply work | Supply of work | As per relevent standard specification | 2055 | SET | 2055 | 24660
38 | SWR11890 | 0.186 | Mass Concreting for pole Coping of 1.5'x1.5'x1 with 1:8 slope Using form boxes (0.031Cumt.) | Civil work | Civil of work | As per relevent standard specification | 3893.01 | M3 | 3893.01 | 724.0999
39 | SMR40045 | 2 | Control Panels Supply of AC Supply panel inluding providing of changeover switch, SFU, metering unit, 32 A three phase MCB, 16 A Single phase MCB complete as per specification | Electrical work | Erection of work | As per relevent standard specification | 42000 | EA | 42000 | 84000
40 | SWR11893 | 2 | Control Panels Erection of control/Relay panels, AC Panels, announciation panels etc in the control room duly mounting them on channels and grouting them with foundation bolts excluding cost of channels & foundation bolts | Electrical work | Erection of work | As per relevent standard specification | 2122 | EA | 2122 | 4244
41 | SMR40011 | 18 | Supply of various Clamps Supply of Alluminum alloy T clamps conforming to A6 of IS 617, 4 bolted with hot dip galvanised bolts and double nuts with spring and flat washers of size M10 x 65 i.e(3/8" x 21/2 " to suit for panther ACSR on all three ways /on one side and Zebra ACSR on take off side or any other combination for carrying 800 A current rating | Supply work | Supply of work | As per relevent standard specification | 299 | EA | 299 | 5382
42 | SMR22473 | 6 | Supply of various Clamps Supply of I Bolts | Supply work | Supply of work | As per relevent standard specification | 294 | EA | 294 | 1764
43 | SMR40009 | 4.4 | Painting Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. | Erection work | Erection of work | As per relevent standard specification | 2181 | TO | 2181 | 9596.4
44 | SWR10877 | 4.4 | Painting Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium | Erection work | Erection of work | As per relevent standard specification | 851 | TO | 851 | 3744.4
45 | SMR40010 | 4.4 | Painting (*)Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. | Erection work | Erection of work | As per relevent standard specification | 1293 | TO | 1293 | 5689.2
46 | SWR10879 | 4.4 | Painting (*) Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium . | Erection work | Erection of work | As per relevent standard specification | 482 | TO | 482 | 2120.8
47 | SWR10920 | 40 | Laying of earth mat including excavation of trenches of depth 600mm, welding, connecting to equipment and connecting lightning shield to earth mat and earthing of fence posts, drilling and connecting earth rods including connecting cast iron pipes with the following sizes of MS Flats /GI Flats. including fabrication 75x 8mm MS Flat / GI Flat. | Earthing work | Earthing of work | As per relevent standard specification | 65 | RMT | 65 | 2600
48 | SWR10919 | 100 | Fabrication and connecting to risers from earth mat to structures, equipment, marshalling boxes, electrical panels, PLCC panels, fencing posts etc. M.S./ G.I. Flat 50x6mm / 50 x 8 mm ( Above ground) | Earthing work | Earthing of work | As per relevent standard specification | 41 | RMT | 41 | 4100
49 | SWR22093 | 30 | Supply of HBG metal Providing of control cable trench as per DATA-XII | Supply work | Supply of work | As per relevent standard specification | 3148 | RMT | 3148 | 94440
50 | SWR12510 | 200 | L-Cable Termination to Switchgear | Electrical work | Erection of work | As per relevent standard specification | 27 | EA | 27 | 5400
51 | SWR11089 | 10 | Painting of poles Paint of coping with 2 coats of white cement incl cost of paints etc. | Erection work | Erection of work | As per relevent standard specification | 48 | EA | 48 | 480
52 | SWR12331 | 4 | Making of coil earthing pole with 8mm GI wireNut&Bolts for AB Switch | Earthing work | Earthing of work | As per relevent standard specification | 146.63 | EA | 146.63 | 586.52
53 | SWR10881 | 4 | Painting Painting of operating rods of 33kV,11kV AB switches with post office red colour (including cost of paint) | Erection work | Erection of work | As per relevent standard specification | 142 | EA | 142 | 568
54 | SWR10860 | 11 | Supply of HBG metalSupply & spreading of 20mm machine crushed metal (HBG) including cost of conveneyance of all materials, labour charges etc complete for finished item of work and directed by the engineer incharge | Supply work | Supply of work | As per relevent standard specification | 2113 | M3 | 2113 | 23243
55 | SWR10743 | 6 | Painting of all suppports to a height of 0.3m coping with bituminous paint (black colour) and painting of coping with two coats of white cement (including cost of paint)Painting of all suppports to a height of 0.3m coping with bituminous paint (black colour) and painting of coping with two coats of white cement (including cost of paint) | Erection work | Erection of work | As per relevent standard specification | 686 | EA | 686 | 4116
56 | SWR10357 | 10 | Providing of Earthing Providing of earthing with excavation of earth pit (0.6 x0.6x2.4 Mts.) duly filling with bentonite, earth , running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.75M dia x 0.5 M height | Earthing work | Earthing of work | As per relevent standard specification | 1234.2 | EA | 1234.2 | 12342
57 | SWR10390 | 8 | Making of Outdoor/Indoor End Termination 11 KV 3x185 Sqmm Cable | Earthing work | Earthing of work | As per relevent standard specification | 2370.63 | EA | 2370.63 | 18965.04
58 | SWR11974 | 150 | Excavation & laying of UG Cable (Double Run) 11 KV 3x185 Sqmm Cable | Earthing work | Earthing of work | As per relevent standard specification | 631.06 | M | 631.06 | 94659
59 | SWR11982 | 110 | Along the CC / BT multi layer road requiring compressor 11 KV 3x185 Sqmm Cable | Earthing work | Earthing of work | As per relevent standard specification | 1264.64 | M | 1264.64 | 139110.4
60 | SWR12006 | 40 | Raising of double run cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe) Raise-DR 11KV 3x185sqmm UG Cb on support11 KV 3x185 Sqmm Cable | Erection work | Erection of work | As per relevent standard specification | 243.53 | M | 243.53 | 9741.2
61 | SMR40080 | 24 | Supply of 4" B class GI pipe Supply of 4" B class GI pipe | Supply work | Supply of work | As per relevent standard specification | 740 | M | 740 | 17760
62 | SMR11480 | 4 | Supply of GI eath pipe with 40 mm dia,3mm thcikness with 2.0 M Length Supply of GI eath pipe with 40 mm dia,3mm thcikness with 2.0 M Length | Supply work | Supply of work | As per relevent standard specification | 698 | EA | 698 | 2792
63 | SMR11485 | 40 | Supply of earthing pipe with materials Supply of GI Flat 25X3 mm | Supply work | Supply of work | As per relevent standard specification | 105 | KG | 105 | 4200
64 | SWR10356 | 6.12 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc.Including the cost of cement | Erection work | Erection of work | As per relevent standard specification | 6579 | M3 | 6579 | 40263.48
65 | SWR10454 | 2.1 | Stringing of HT AB Cable with GI Metal Parts HT AB Cable 11 KV 3x185+70 Sqmm | Erection work | Erection of work | As per relevent standard specification | 41876.1 | KM | 41876.1 | 87939.81
66 | SMR11485 | 82 | Supply of GI Flat 25X3 mm Supply of GI Flat 25X3 mm | Supply work | Supply of work | As per relevent standard specification | 105 | KG | 105 | 8610
67 | SWR11037 | 10 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders) 0.76 M x 0.76M x 1.52M (2.6" x 2.6" x 5.0') 0.88 cum | Erection work | Erection of work | As per relevent standard specification | 793 | EA | 793 | 7930
68 | SMR11504 | 30 | End Termination of AB cable (each lead): Supply of 11KV 3x185+70sq.mm / 3x70+70sq.mm/3x35+35sq.mm AB cable end Kits | Erection work | Erection of work | As per relevent standard specification | 950 | SET | 950 | 28500
69 | SWR10667 | 30 | End Termnatn of AB cable 120 to 185 Sqmm | Erection work | Erection of work | As per relevent standard specification | 800 | EA | 800 | 24000
70 | SMR12099 | 86 | Supply- I Hook | Supply work | Supply of work | As per relevent standard specification | 158 | EA | 158 | 13588
71 | SWR12099 | 86 | Supply and Erection of I Hook and Suspension Hook Erection of I hook | Supply work | Supply of work | As per relevent standard specification | 55 | EA | 55 | 4730
72 | SMR40091 | 7 | Earthing of Sub-StationSupply of GI pipe 40 mm dia, 2 mtrs, 3mm thickness with bolts and nuts | Earthing work | Earthing of work | As per relevent standard specification | 733 | EA | 733 | 5131
73 | SWR10357 | 7 | Providing of Earthing Providing of earthing with excavation of earth pit (0.6 x0.6x2.4 Mts.) duly filling with bentonite, earth , running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.75M dia x 0.5 M height | Earthing work | Earthing of work | As per relevent standard specification | 1234.2 | EA | 1234.2 | 8639.4
74 | SWR10671 | 6 | T Branch Kit Erection of Assemble Kit for 'T' Branche | Erection work | Erection of work | As per relevent standard specification | 1800 | EA | 1800 | 10800
75 | SWR24971 | 6 | T Branch Kit Supply and erection of T-Branch kit | Erection work | Erection of work | As per relevent standard specification | 3215 | EA | 3215 | 19290
76 | SWR10673 | 14 | Straight through joints of AB cable (each lead) Supply and ere Angle line Asmbly kits | Erection work | Erection of work | As per relevent standard specification | 2124 | EA | 2124 | 29736
77 | SWR11862 | 5 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)Above 20 Km and upto 30 Km with Lorry for each trip | Erection work | Erection of work | As per relevent standard specification | 3691.38 | EA | 3691.38 | 18456.9
78 | SWR12413 | 4 | Loading of 11 KV AB Cable (XLPE) 3 Core upto 500 Mts. Drum (including Accessories ) | Loading work | Loading of work | As per relevent standard specification | 584 | DR | 584 | 2336
79 | SWR12431 | 4 | Un loading of 11 KV AB Cable (XLPE) 3 Core upto 500 Mts.Drum (including Accessories ) | Un loading work | Un loading of work | As per relevent standard specification | 438 | DR | 438 | 1752
80 | SMR11488 | 195 | Supply of earthing pipe with materials Supply of GI Bolts & Nuts etc | Supply work | Supply of work | As per relevent standard specification | 117.5 | KG | 117.5 | 22912.5
81 | SMR40132 | 30 | Supply of 120 Sqmm Aluminium lugs | Supply work | Supply of work | As per relevent standard specification | 12.52 | EA | 12.52 | 375.6
82 | SWR10356 | 45.5 | Mass concreting of supports incl. cement | Civil work | Civil of work | As per relevent standard specification | 6579 | M3 | 6579 | 299344.5
83 | SWR10320 | 156 | Fabrication of materials including 2 coats of Red oxide painting Back clamps with 50 x 6 mm MS Flat | Erection work | Erection of work | As per relevent standard specification | 15 | EA | 15 | 2340
84 | SWR10653 | 3 | Formation of Cut points Formation of Cut point for 11 KV Single Circuit line excluding pole erection and stays | Erection work | Erection of work | As per relevent standard specification | 1435.81 | EA | 1435.81 | 4307.43
85 | SWR10672 | 72 | Straight through joints of AB cable (each lead) Supply and ere Straight line Asmbly kits | Erection work | Erection of work | As per relevent standard specification | 1661 | EA | 1661 | 119592
86 | SWR10393 | 2 | Erection of AB Switch and aligment complete Erection of 11KV 400/200A Conventional type AB Switch including fixing of cross angles and alignment complete | Erection work | Erection of work | As per relevent standard specification | 3200 | EA | 3200 | 6400
87 | SWR10343 | 15 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation9.1 M long PSCC pole | Erection work | Erection of work | As per relevent standard specification | 2400 | EA | 2400 | 36000
88 | SWR20308 | 15 | MATERIALS AND EQUIPMENTS Sub-transport of poles upto Workspot upto 10KM (Including loading and unloading 9.1 Mtrs long PSCC Poles | Erection work | Erection of work | As per relevent standard specification | 407.29 | EA | 407.29 | 6109.35
89 | SWR10666 | 0.35 | Stringing of LT AB Cable LT AB cable 3x70 + 1x16 + 1x50 | Stringing work | Stringing of work | As per relevent standard specification | 8450 | KM | 8450 | 2957.5
90 | SWR22065 | 0.35 | Dismantling of Line Dismantling of 11KV 34/55 sqmm SC | Dismantling work | Dismantling of work | As per relevent standard specification | 4500 | KM | 4500 | 1575
91 | SWR10642 | 4 | Fabrication of poles: Fabrication of 175x85/150x75mm RS joist pieces upto 12.5 meters length by welding joint together by means of 50x6mm flat and MS channel on either side including the cost of consumable. | Fabrication work | Fabrication of work | As per relevent standard specification | 512.55 | EA | 512.55 | 2050.2
92 | SWR11720 | 10 | Fabrication of poles:11KV side arm 75x40mm Channel 65x65x6mm Angle | Fabrication work | Fabrication of work | As per relevent standard specification | 100 | EA | 100 | 1000
93 | SWR11038 | 9 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders)0.6 M x 0.9 M x 1.5 M (0.81 cubmic meter) | Excavation work | Excavation of work | As per relevent standard specification | 612 | EA | 612 | 5508
94 | SWR11266 | 4 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation Box pole 9/10/11 Mtr | Erection work | Erection of work | As per relevent standard specification | 2643.83 | EA | 2643.83 | 10575.32
95 | SWR11269 | 10 | Fixing of Side Arm along with Cross Arm including angle strut up to 5 feet 11KV | Erection work | Erection of work | As per relevent standard specification | 455 | EA | 455 | 4550
96 | SWR10640 | 4 | Painting of poles Painting of R.S Joist,Box poles including cross arms and clamps with one coat of red oxid and two coats of Al.paint including cost of paint and consumables | Erection work | Erection of work | As per relevent standard specification | 1132 | EA | 1132 | 4528
97 | SMR25160 | 32 | S-Insulating Piercing Connector | Supply work | Erection of work | As per relevent standard specification | 1050 | EA | 1050 | 33600
98 | SWR21914 | 32 | Supply and Erection of I Hook and Suspension Hook Erection of Insulated Connectors with covers | Supply work | Erection of work | As per relevent standard specification | 80 | EA | 80 | 2560
99 | SWR12125 | 50 | Providing of RCC collar to earth pit. Running of GI eartn flat of size 25X3mm from all metallic parts of channels, AB Switch, HG fuse set, DTr neutral and LT Distribution box and inter connection of earth pits etc complete | Earthing work | Earthing of work | As per relevent standard specification | 14.03 | M | 14.03 | 701.5
100 | SMR11486 | 6 | Supply of earthing pipe with materials Supply of GI wire No 8 | Supply work | Earthing of work | As per relevent standard specification | 105 | KG | 105 | 630
101 | SWR10204 | 10 | Loading and Unloading Loading of R.S. Joists 175 x 85 mm | Loading work | Loading of work | As per relevent standard specification | 76 | EA | 76 | 760
102 | SWR11180 | 30 | SubTrnsprt 11M PSCC Pole incl. L&UL<10KM | Erection work | Erection of work | As per relevent standard specification | 431.97 | EA | 431.97 | 12959.1
103 | SWR10522 | 10 | Loading and Unloading Un loading of R.S. Joists 175 x 85 mm | Un loading work | Un loading of work | As per relevent standard specification | 50 | EA | 50 | 500
104 | SWR10206 | 0.5 | Loading and Unloading Loading of M.S.Channels, Angles, Flats & Rods etc., | Loading work | Loading of work | As per relevent standard specification | 221 | TO | 221 | 110.5
105 | SWR10524 | 0.5 | Loading and Unloading Un loading of M.S.Channels, Angles, Flats & Rods etc., | Un loading work | Un loading of work | As per relevent standard specification | 185 | TO | 185 | 92.5
106 | SWR11248 | 45 | Loading and Unloading Loading of 11KV Polymer Pin Insulators with GI pins | Loading work | Loading of work | As per relevent standard specification | 1 | EA | 1 | 45
107 | SWR11249 | 45 | Un loading of 11KV Polymer Pin Insulators with GI pins | Un loading work | Un loading of work | As per relevent standard specification | 1 | EA | 1 | 45
108 | SWR10298 | 8 | Cutting charges for MS Sections RS Joists 175 x 85 mm | Erection work | Erection of work | As per relevent standard specification | 47 | EA | 47 | 376
109 | SWR10227 | 2 | LOADING of 33 KV V - Cross arms | Electrical work | Erection of work | As per relevent standard specification | 6 | EA | 6 | 12
110 | SWR10545 | 2 | UNLOADING of 33 KV V - Cross arms | Electrical work | Erection of work | As per relevent standard specification | 6 | EA | 6 | 12
111 | SWR10261 | 7 | Condu. Winding Dog and rabbi | Electrical work | Erection of work | As per relevent standard specification | 237 | KM | 237 | 1659
112 | SWR10579 | 7 | UNLOADING of Un winding of conductor including weighing per KM dog & rabbit | Electrical work | Erection of work | As per relevent standard specification | 237 | KM | 237 | 1659
113 | SWR10238 | 1 | LOADING of 11 KV AB SWCH Con 200/400 A | Electrical work | Erection of work | As per relevent standard specification | 80 | EA | 80 | 80
114 | SWR10556 | 1 | UNLOADING of 11 KV AB SWCH Con 200/400 A | Electrical work | Erection of work | As per relevent standard specification | 80 | EA | 80 | 80
115 | SWR10298 | 4 | Cutting Charges for RS joist 175x85mm | Electrical work | Erection of work | As per relevent standard specification | 47 | EA | 47 | 188
116 | SWR10301 | 60 | Cutting charges for MS Sections MS flat of all sizes | Electrical work | Erection of work | As per relevent standard specification | 2 | EA | 2 | 120
117 | SWR10319 | 60 | Fab Back clamps with 75 x 8 mm MS Flat | Electrical work | Erection of work | As per relevent standard specification | 31 | EA | 31 | 1860
118 | SWR10320 | 80 | Fabrication of materials including 2 coats of Red oxide painting Back clamps with 50 x 6 mm MS Flat | Electrical work | Erection of work | As per relevent standard specification | 15 | EA | 15 | 1200
119 | SWR10640 | 1 | Painting of R.S Joist,Box poles including cross arms and clamps with one coat of red oxid and two coats of Al.paint including cost of paint and consumables | Electrical work | Erection of work | As per relevent standard specification | 1132 | EA | 1132 | 1132
120 | SWR11720 | 60 | 11KV side arm 75x40mm Channel 65x65x6mm Angle | Electrical work | Erection of work | As per relevent standard specification | 100 | EA | 100 | 6000
121 | SWR11269 | 60 | Fixing of Side Arm along with Cross Arm including angle strut up to 5 feet 11KV | Electrical work | Erection of work | As per relevent standard specification | 455 | EA | 455 | 27300
122 | SWR10653 | 3 | Formation of Cut point for 11 KV Single Circuit line excluding pole erection and stays | Electrical work | Erection of work | As per relevent standard specification | 1435.81 | EA | 1435.81 | 4307.43
123 | SWR10642 | 1 | Fabrication of 175x85/150x75mm RS joist pieces upto 12.5 meters length by welding joint together by means of 50x6mm flat and MS channel on either side including the cost of consumable. | Electrical work | Erection of work | As per relevent standard specification | 512.55 | EA | 512.55 | 512.55
124 | SWR11266 | 1 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation Box pole 9/10/11 Mtr | Electrical work | Erection of work | As per relevent standard specification | 2643.83 | EA | 2643.83 | 2643.83
125 | SWR10365 | 2 | Paving out and stringing of conductor by providing temporary stays, tensioning, sagging correctly, fixing strain points, transferring to pin points binding, keeping stifner, rectification of poles, guys and jumpering etc., including transport of material from road side to location.55 Sqmm Single Circuit (3 Conductors) | Electrical work | Erection of work | As per relevent standard specification | 9454.81 | KM | 9454.81 | 18909.62
126 | SWR22063 | 2 | Dismantling of 100 Sqmm AAA/ACSR Conductor | Electrical work | Erection of work | As per relevent standard specification | 8274.75 | KM | 8274.75 | 16549.5
127 | SWR10981 | 6 | Formation of Cut point for 33 KV Single Circuit line excluding pole erection and stays | Electrical work | Erection of work | As per relevent standard specification | 1791.12 | EA | 1791.12 | 10746.72
128 | SWR10366 | 2 | Paving out and stringing of conductor by providing temporary stays, tensioning, sagging correctly, fixing strainpoints, transferring to pin points binding, keeping stifner, rectification of poles, guys and jumpering etc., including transport of material from road side to location.100 Sqmm Single Circuit (3 Conductors) | Electrical work | Erection of work | As per relevent standard specification | 13856.7 | KM | 13856.7 | 27713.4
129 | SWR23200 | 2500 | Cut-Tree Branch(LT/11/33)&Trnsprt Debris | Electrical work | Erection of work | As per relevent standard specification | 4 | EA | 4 | 10000
130 | SWR11040 | 20 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders)0.75 M x 0.9 M x 1.95 M | Electrical work | Erection of work | As per relevent standard specification | 990.68 | EA | 990.68 | 19813.6
131 | SWR10113 | 10 | Excavation of pits in hard rock requiring blasting. (other than SS)0.75 M x 0.9 M x 1.95 M | Electrical work | Erection of work | As per relevent standard specification | 1326 | EA | 1326 | 13260
Schedule Cost. (Excluding GST) | [9 empty] | 1951788.7199