## Padma Nagar feeder
Schedule (WBS No.T-2432-07-05-01-02-005 and T-2432-07-05-01-02-001)
Name of the work: Bifurcation of existing 11KV Maisammaguda feeder emanating from 33/11KV G.P.Pally SS by proposing 1.80KM of new 11KV feeder from the same SS with stringing of 1.8KM of 55Sqmm. AAA Conductor on 11mts & 9.1Mtr PSCC poles & laying of 190 mtrs (D.Run) of 11KV XLPE 3X185Sqmm UG Cable duly erecting additional 1No. 11KV Bay & Breaker at 33/11KV G.P.Pally SS in G.P.Pally Section & Providing of new 11KV feeder from 33/11KV HMT SS with stringing of 2345 mtrs of 11KV 3X185+70Sq.mm. AB cable over now proposed 24 No of 9.1mtr PSCC poles and existing 100 Poles along with erection of 1No. 11KV Bay & Breaker for bifurcation existing 11KV Padma Nagar feeder emanating from 33/11KV Subhash nagar SS of Medchal Sub-Division of Medchal division and the work executed by Construction Division of Medchal Circle under T&D Improvement to Original Works (Summer Action Plan-2025 works).
Sl.No. | SSR CODES | Estimate Quantity (Only figures) | Particulars | Work Type eg., Earth Work, Electrical works..etc., (Upto 200 Characters) | Item Short Description | APSS/Morth CI.Number (Upto 200 characters) | Rate INR upto 2 Decimals | UOM (upto 50 Characters) | Amount INR (Upto 2 Decimals)
1 | SWR10461 | 2 | Erection of AB Switches, VCBs, LAs, PTs, CTs, DTRs etc Erection of 11 KV VCB with Control Panel | Erection work | Erection of work | As per relevent standard specification | 12000 | EA | 24000
2 | SMR11482 | 7 | Supply of earthing pipe with materials iii)Supply of CI earth pipe 100 mm dia, 2.75 mt long thickness 10mm with flange as per specication | Supply work | Supply of work | As per relevent standard specification | 3486 | EA | 24402
3 | SWR10356 | 16.7 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand,Cement and curing etc.Including the cost of cement | Erection work | Erection of work | As per relevent standard specification | 6579 | M3 | 109869.3
4 | SWR11879 | 1100 | Laying of 4 core/10 core 2.5 sq. mm.Copper control cable in aready excavation trench including cost of providing single compress glands at both ends . | Erection work | Erection of work | As per relevent standard specification | 27 | M | 29700
5 | SMR11488 | 95 | Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50 M height | Erthing work | Erthing of work | As per relevent standard specification | 117.5 | KG | 11162.5
6 | SWR10942 | 1 | Testing of Sub-Station Equipment Wirring, commissioning and testing of Outdoor Sub-station switchgear duly conducting the pre commissioning test as per relevent standards & issue of certificate by CEIG authorised testing Engineer | Erection work | Erection of work | As per relevent standard specification | 1825 | EA | 1825
7 | SWR12092 | 2 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders)(0.75M x 0.75M x 2.5M) 1.406 cum | Excavation work | Excavation of work | As per relevent standard specification | 1063.35 | EA | 2126.7
8 | SWR10238 | 6 | LOADING of LINE MATERIALS 11 KV AB SWCH Con 200/400 A | LOADING work | LOADING of work | As per relevent standard specification | 80 | EA | 480
9 | SWR10917 | 30 | Fixing of Side Arm along with Cross Arm including angle strut up to 5 feet 11KV | Erection work | Erection of work | As per relevent standard specification | 65 | EA | 1950
10 | SWR10393 | 6 | Erection of AB Switch and aligment complete Erection of 11KV 400/200A Conventional type AB Switch including fixing of cross angles and alignment complete | Erection work | Erection of work | As per relevent standard specification | 3200 | EA | 19200
11 | SWR11861 | 2 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels,current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading) Note: 1). It will be treated as full load of 10 MT and paid for 10 MT. 2). For 3 Ton vehicle : 50% of the following rates Above 10 Km and upto 20 Km with Lorry for each trip | Transport work | Transport of work | As per relevent standard specification | 3299.7 | EA | 6599.4
12 | SWR10199 | 2 | LOADING of LINE MATERIALS 11 KV VCBs&Panel boards | LOADING work | LOADING work | As per relevent standard specification | 1024 | EA | 2048
13 | SWR10517 | 2 | UNLOADING of LINE MATERIALS 11 KV VCBs&Panel boards | LOADING work | LOADING work | As per relevent standard specification | 1044.48 | EA | 2088.96
14 | SWR10556 | 6 | UNLOADING of LINE MATERIALS 11 KV AB SWCH Con 200/400 A | LOADING work | LOADING work | As per relevent standard specification | 80 | EA | 480
15 | SWR10348 | 2 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports,back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation R.S. Joists 150 x 150 mm | Erection work | Erection work | As per relevent standard specification | 1952.61 | EA | 3905.22
16 | SWR10205 | 5 | LOADING of LINE MATERIALS RSJoists150 x 150 mm/RailPole | LOADING work | LOADING wor | As per relevent standard specification | 176 | EA | 880
17 | SWR10523 | 5 | UNLOADING of LINE MATERIALS RSJoists150 x150 mm/RailPol | LOADING work | LOADING work | As per relevent standard specification | 107 | EA | 535
18 | SWR10206 | 2.52 | LOADING of LINE MATERIALS MS Channel,Angles,Flats&Rods | LOADING work | LOADING work | As per relevent standard specification | 221 | TO | 556.92
19 | SWR10524 | 2.52 | UNLOADING of LINE MATERIALS MS Channel,Angles,Flats&Rod | LOADING work | LOADING work | As per relevent standard specification | 185 | TO | 466.2
20 | SWR10265 | 3 | LOADING of LINE MATERIALS 11 KV, 10 KA LAs Line type | LOADING work | LOADING work | As per relevent standard specification | 32 | EA | 96
21 | SWR10583 | 3 | UNLOADING of LINE MATERIALS 11 KV, 10 KA LAs Line type | LOADING work | LOADING work | As per relevent standard specification | 32 | EA | 96
22 | SWR11701 | 450 | LOADING of LINE MATERIALS PVC Control Cable 10C | LOADING work | LOADING work | As per relevent standard specification | 1 | M | 450
23 | SWR11712 | 450 | UNLOADING of LINE MATERIALS PVC Control Cable 10C | LOADING work | LOADING work | As per relevent standard specification | 1.02 | M | 459
24 | SWR10297 | 9 | Cutting charges for MS Sections RS Joists 150 x 150 mm | Erection work | Erection work | As per relevent standard specification | 48 | EA | 432
25 | SWR10307 | 40 | Drilling of holes upto 20 mm dia using power drills MS Channel, Angles and flat | Erection work | Erection work | As per relevent standard specification | 4 | EA | 160
26 | SWR10359 | 11 | Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50 M height | Erection work | Erection work | As per relevent standard specification | 386 | EA | 4246
27 | SWR12294 | 0.25 | Excavatin of pit Providing of Base Concreting (Pole pits- 076 M x 0.76M x 0.15M ) with 1:3:6 Concrete Mix including curing with water | Excavation work | Excavation of work | As per relevent standard specification | 5053 | M3 | 1263.25
28 | SWR10868 | 1.05 | Fabrication of Main and Auxiliary structures with power drilling using raw steel such as M.S.Angles, Plates, Channels, R.S.Joists, including the supply and fabrication of 6mm base and top plate for Box pole to the RSJoist poles excluding cost of Mild Steel and transport charges to substation site, including erection. | Fabrication work | Fabrication of work | As per relevent standard specification | 6852 | TO | 7194.6
29 | SWR10867 | 1.05 | Alligning the Main and Auxiliary structures such as RS joist, M.S.Angles, Plates, Channels, Structure to zero level duly leveling in prefabricated MS frames with Hydraulic jacks before galvanising/ fabrication. | Civil work | Civil work | As per relevent standard specification | 1470 | TO | 1543.5
30 | SWR21241 | 1 | Hoisting of Insulators and hardware, stretching the conductor and stringing of 11 kV bus comprising of three phases with Single Zebra/panther conductor to a tension of 450kgs.(Bus section of 3.5mt) | Civil work | Civil work | As per relevent standard specification | 507 | EA | 507
31 | SMR11915 | 6 | Supply of Tension Hardware 3 Bolted for single Zebra/panther with 150 mm spacing. | Supply work | Supply of work | As per relevent standard specification | 2055 | SET | 12330
32 | SWR11890 | 0.093 | Mass Concreting for pole Coping of 1.5'x1.5'x1 with 1:8 slope Using form boxes (0.031Cumt.) | Civil work | Civil work | As per relevent standard specification | 3893.01 | M3 | 362.0499
33 | SMR40011 | 9 | Supply of clamps as per IS 5561- 1970 , 12mm thickness with Alluminum and Alluminum alloy Supply of Alluminum alloy T clamps conforming to A6 of IS 617, 4 bolted with hot dip galvanised bolts and double nuts with spring and flat washers of size M10 x 65 i.e(3/8" x 21/2 " to suit for panther ACSR on all three ways /on one side and Zebra ACSR on take off side or any other combination for carrying 800 A current rating | Erection work | Erection work | As per relevent standard specification | 299 | EA | 2691
34 | SMR22473 | 3 | Supply of clamps as per IS 5561- 1970 , 12mm thickness with Alluminum and Alluminum alloy Supply of I Bolts | Supply work | Supply of work | As per relevent standard specification | 294 | EA | 882
35 | SMR40009 | 2.2 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1stgrade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied Supply of material cost for First coat of 1st Grade Aluminium Paint,brushes etc. | Painting work | Painting of work | As per relevent standard specification | 2181 | TO | 4798.2
36 | SWR10877 | 2.2 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1stgrade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied Labour charges for painting including scratching and cleaning of Substationstructures of 1st coat of Aluminium | Painting work | Painting of work | As per relevent standard specification | 851 | TO | 1872.2
37 | SMR40010 | 2.2 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1stgrade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied (*)Supply of material cost for Second coat of 1st Grade Aluminium Paint brushes, etc. | Painting work | Painting of work | As per relevent standard specification | 1293 | TO | 2844.6
38 | SWR10879 | 2.2 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1stgrade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied Labour charges for painting including scratching and cleaning of Substation structures of 2nd coat of Aluminium . | Painting work | Painting of work | As per relevent standard specification | 482 | TO | 1060.4
39 | SWR10920 | 45.53 | Laying of earth mat including excavation of trenches of depth 600mm, welding, connecting to equipment and connecting lightning shield to earth mat and earthing of fence posts, drilling and connecting earth rods including connecting cast iron pipes with the following sizes of MS Flats /GI Flats. including fabrication.75x 8mm MS Flat / GI Flat. | Earthing work | Earthing of work | As per relevent standard specification | 65 | RMT | 2959.45
40 | SWR10919 | 50 | Fabrication and connecting to risers from earth mat to structures, equipment,marshalling boxes, electrical panels, PLCC panels, fencing posts etc.M.S./ G.I. Flat 50x6mm / 50 x 8 mm ( Above ground) | Fabrication work | Fabrication of work | As per relevent standard specification | 41 | RMT | 2050
41 | SWR12510 | 100 | L-Cable Termination to Switchgear | Erection work | Erection work | As per relevent standard specification | 27 | EA | 2700
42 | SWR11089 | 5 | Painting of poles Paint of coping with 2 coats of white cement incl cost of paints etc. | Painting work | Painting of work | As per relevent standard specification | 48 | EA | 240
43 | SWR12331 | 6 | Making of coil earthing pole with 8mm GI wireNut&Bolts for AB Switch | Earthing work | Earthing of work | As per relevent standard specification | 146.63 | EA | 879.78
44 | SWR10881 | 6 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied Painting of operating rods of 33kV, 11kV AB switches with post office red colour (including cost of paint) | Painting work | Painting of work | As per relevent standard specification | 142 | EA | 852
45 | SWR10860 | 5.5 | Supply of HBG metal Supply & spreading of 20mm machine crushed metal (HBG) including cost of conveneyance of all materials, labour charges etc complete for finished item of work and directed by the engineer incharge | Supply work | Supply of work | As per relevent standard specification | 2113 | M3 | 11621.5
46 | SWR10743 | 2 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied Painting of all suppports to a height of 0.3m coping with bituminous paint (black colour) and painting of coping with two coats of white cement (including cost of paint) | Painting work | Painting of work | As per relevent standard specification | 686 | EA | 1372
47 | SWR10357 | 7 | Providing of earthing with excavation of earth pit (0.6x0.6x2.4 Mts.) duly filling with bentonite, earth ,running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.6M dia x 0.5 M height . | Supply work | Supply of work | As per relevent standard specification | 1234.2 | EA | 8639.4
48 | SMR11485 | 50 | Supply of earthing pipe with materials Supply of GI Flat 25X3 mm | Supply work | Supply of work | As per relevent standard specification | 105 | KG | 5250
49 | SMR11435 | 2 | PROTECTION WORK - Supply of Plain switches | Supply work | Supply of work | As per relevent standard specification | 30 | EA | 60
50 | SWR11435 | 2 | PROTECTION WORK - Fixing of Plain switches | Supply work | Supply of work | As per relevent standard specification | 13 | EA | 26
51 | SMR11524 | 4 | PROTECTION WORK - Supply of Indication LED Lamps 250 V DC (White,blue, Amber) Diameter 22.5 mm suitable for fixing in Control Relay Panels of Circuit Breakers. | Supply work | Supply of work | As per relevent standard specification | 130 | EA | 520
52 | SMR11914 | 2 | PROTECTION WORK - Supply of Push buttons (with NO contact) self illuminating LED 250 V DC White Diameter 22.5 mm suitable for fixing in Tripping Circuit Healthy Circuit in Control Relay Panels of CircuitBreakers. 220VDC Illuminating Healthy Trip Push Button | Supply work | Supply of work | As per relevent standard specification | 300 | EA | 600
53 | SWR11380 | 1 | PROTECTION WORK - Fixing of Hylam Sheet & Cutting of Panel & Fixing of relay | Supply work | Supply of work | As per relevent standard specification | 2000 | EA | 2000
54 | SWR20768 | 3.888 | Earth work excavation of in all soils except hard rock requiring blasting. | Earthing work | Earthing of work | As per relevent standard specification | 345 | M3 | 1341.36
55 | SWR10732 | 1 | Con of Plinth for 11kv VCB 1.8x1.8x0.75m | Earthing work | Earthing of work | As per relevent standard specification | 27629 | EA | 27629
56 | SWR10869 | 1.05 | Fabrication of Main and Auxiliary structures with welding using raw steel such as RS joist, M.S.Angles, Plates, Channels, including the supply and fabrication of 6mm base plate to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection. | Fabrication work | Fabrication of work | As per relevent standard specification | 3426 | TO | 3597.3
57 | SWR10133 | 3.22 | Transport of iron materials such as R.S. Joists, Rail Poles, fabricated supports, steel, iron, flat, M.S.Channels etc., by lorries. (excluding of loading & unloading )Above 20 KM and upto 30 KM | Transport work | Transport of work | As per relevent standard specification | 476.34 | TO | 1533.8148
58 | SWR11862 | 3 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels,current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)Above 20 Km and upto 30 Km with Lorry for each trip | Transport work | Transport of work | As per relevent standard specification | 3691.38 | EA | 11074.14
59 | SWR11891 | 10 | Laying of earth mat including excavation of trenches of depth 600mm,welding, connecting to equipment and connecting lightning shield to earth mat and earthing of fence posts, drilling and connecting earth rods including connecting cast iron pipes with the following sizes of MS Flats /GI Flats. including fabrication.Connecting with GI Wire No.8 (Labour) | Earthing work | Earthing of work | As per relevent standard specification | 14 | M | 140
60 | SWR23105 | 550 | SS works L-PVC Control Cb 4, 10C | Supply work | Supply of work | As per relevent standard specification | 1 | M | 550
61 | SWR23106 | 550 | SS works UL-PVC Control Cb 4, 10C | Supply work | Supply of work | As per relevent standard specification | 0.15 | M | 82.5
62 | SWR10391 | 4 | Making of Outdoor/Indoor End Termination 11 KV 3x300 Sqmm Cable | Supply work | Supply of work | As per relevent standard specification | 2370.63 | EA | 9482.52
63 | SWR20863 | 2 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports,back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation Erection of 5 Mts RS Joist (Bit) Pole including fixing of Pole Mounted Box | Erection work | Erection of work | As per relevent standard specification | 1044.23 | EA | 2088.46
64 | SWR11973 | 50 | Laying of XLPE UG cable Double Run including excavation of trench of size 600mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV from road level and cable separation with machine cut bricks horizontally for every 3 meters , providing of DWC/GI pipes wherever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth,levelling and removing the debris from the site inluding the cost of lead and lift etc.. (Second cable laying cost not Included) depth of the trench LT-0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs.11 KV 3x300 Sqmm Cable | Excavation work | Excavation of work | As per relevent standard specification | 631.06 | M | 31553
65 | SWR12005 | 20 | Raising of double run cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe)11 KV 3x300 Sqmm Cable | Erection work | Erection of work | As per relevent standard specification | 275.4 | M | 5508
66 | SWR10884 | 2 | Bus Stringing Connection of equipment to bus and or another equipment with single zebra/Panther conductor including measuring, cutting,clamping and hoisting of suspension insulator assembly to support the conductor wherever necessary. | Erection work | Erection of work | As per relevent standard specification | 224 | EA | 448
67 | SWR10988 | 200 | Laying of the cable along the footpath through 225mm dia GI pipe for 33KV, 150mm dia GI pipe for 11KV (excluding the cost of GI pipe)11 KV 3x185 Sqmm Cable | Erection work | Erection of work | As per relevent standard specification | 204.1 | M | 40820
68 | SMR40011 | 6 | Supply of clamps as per IS 5561- 1970 , 12mm thickness with Alluminum and Alluminum alloy Supply of Alluminum alloy T clamps conforming to A6 of IS 617, 4 bolted with hot dip galvanised bolts and double nuts with spring and flat washers of size M10 x 65 i.e(3/8" x 21/2 " to suit for panther ACSR on all three ways /on one side and Zebra ACSR on take off side or any other combination for carrying 800 A current rating | Supply work | Supply of work | As per relevent standard specification | 299 | EA | 1794
69 | SMR40091 | 5 | Earthing of Sub-Station Supply of GI pipe 40 mm dia, 2 mtrs, 3mm thickness with bolts and nuts | Earthing work | Earthing of work | As per relevent standard specification | 733 | EA | 3665
70 | SWR10357 | 5 | Providing of earthing with excavation of earth pit (0.6x0.6x2.4 Mts.) duly filling with bentonite, earth ,running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.6M dia x 0.5 M height . | Earthing work | Earthing of work | As per relevent standard specification | 1234.2 | EA | 6171
71 | SWR10356 | 30 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand,Cement and curing etc.Including the cost of cement | Civil work | Civil work | As per relevent standard specification | 6579 | M3 | 197370
72 | SMR11488 | 100 | Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50 M height | Earthing work | Earthing of work | As per relevent standard specification | 117.5 | KG | 11750
73 | SMR40133 | 30 | S-185Sqmm Alluminium Lug | Supply work | Supply of work | As per relevent standard specification | 13 | EA | 390
74 | SWR10319 | 40 | Fabrication of materials including 2 coats of Red oxide painting Back clamps with 75 x 8 mm MS Flat | Fabrication work | Fabrication of work | As per relevent standard specification | 31 | EA | 1240
75 | SWR10343 | 24 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports,back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation 9.1 M long PSCC pole | Erection work | Erection of work | As per relevent standard specification | 2400 | EA | 57600
76 | SWR10107 | 12 | Excavation of pits in all soils except hard rock requiring blasting 0.76 M x 0.76M x 1.83M (2.6" x 2.6" x 6.0") 1.05 cum | Excavation work | Excavation of work | As per relevent standard specification | 700 | EA | 8400
77 | SWR20308 | 24 | Sub-transport of poles upto Workspot upto 10KM (Including loading and unloading)9.1 Mtrs long PSCC Poles | Civil work | Civil work | As per relevent standard specification | 407.29 | EA | 9774.96
78 | SWR24971 | 6 | T-Branch kit Supply and erection of T-Branch kit | Supply work | Supply of work | As per relevent standard specification | 3215 | EA | 19290
79 | SMR11504 | 30 | End Termination of AB cable (each lead):Supply of 11KV 3x185+70sq.mm/3x70+70sq.mm/3x35+35sq.mm AB cable end Kits | Erection work | Erection of work | As per relevent standard specification | 950 | SET | 28500
80 | SWR10667 | 30 | End Termination of AB cable (each lead):120 Sqmm to 185 Sqmm | Erection work | Erection of work | As per relevent standard specification | 800 | EA | 24000
81 | SWR10673 | 27 | Straight through joints of AB cable (each lead)Supply and ere Angle line Asmbly kits | Supply work | Supply of work | As per relevent standard specification | 2124 | EA | 57348
82 | SMR12099 | 124 | Supply and Erection of I Hook and Suspension Hook Supply of I hook | Supply work | Supply of work | As per relevent standard specification | 158 | EA | 19592
83 | SWR12099 | 124 | Supply and Erection of I Hook and Suspension Hook Erection of I hook | Supply work | Supply of work | As per relevent standard specification | 55 | EA | 6820
84 | SWR10454 | 2.55 | Stringing of HT AB Cable with GI Metal Parts HT AB Cable 11 KV 3x185+70 Sqmm | Erection work | Erection of work | As per relevent standard specification | 41876.1 | KM | 106784.055
85 | SWR10672 | 97 | Straight through joints of AB cable (each lead)Supply and ere Straight line Asmbly kits | Erection work | Erection of work | As per relevent standard specification | 1661 | EA | 161117
86 | SMR11485 | 70 | Supply of earthing pipe with materials iii)Supply of CI earth pipe 100 mm dia, 2.75 mt long thickness 10mm with flange as per specication | Supply work | Supply of work | As per relevent standard specification | 105 | KG | 7350
87 | SWR10206 | 5.5 | LOADING of LINE MATERIALS MS Channel,Angles,Flats&Rods | LOADING work | LOADING of work | As per relevent standard specification | 221 | TO | 1215.5
88 | SWR10524 | 5.5 | UNLOADING of LINE MATERIALS MS Channel,Angles,Flats&Rod | UNLOADING work | UNLOADING of work | As per relevent standard specification | 185 | TO | 1017.5
89 | SWR12413 | 5 | LOADING of LINE MATERIALS 11 KV AB Cable (XLPE) 3 Core | LOADING work | LOADING of work | As per relevent standard specification | 584 | DR | 2920
90 | SWR12431 | 5 | UNLOADING of LINE MATERIALS 11 KV AB Cable (XLPE) 3 Cor | UNLOADING work | UNLOADING of work | As per relevent standard specification | 438 | DR | 2190
91 | SWR11248 | 39 | LOADING of LINE MATERIALS 11KV Polymer Pin Insulator-GI pin | LOADING work | LOADING of work | As per relevent standard specification | 1 | EA | 39
92 | SWR11249 | 39 | UNLOADING of LINE MATERIALS 11KV Polymer Pin Insulator-GI pin | UNLOADING work | UNLOADING of work | As per relevent standard specification | 1 | EA | 39
93 | SWR10294 | 110 | Cutting charges for MS Sections MS Channel 100 x 50 mm | Civil work | Civil work | As per relevent standard specification | 10 | EA | 1100
94 | SWR10301 | 30 | Cutting charges for MS Sections MS flat of all sizes | Civil work | Civil work | As per relevent standard specification | 2 | EA | 60
95 | SWR10320 | 40 | Fabrication of materials including 2 coats of Red oxide painting Back clamps with 50 x 6 mm MS Flat | Fabrication work | Fabrication of work | As per relevent standard specification | 15 | EA | 600
96 | SWR11720 | 13 | 11KV side arm 75x40mm Channel 65x65x6mm Angle | Civil work | Civil work | As per relevent standard specification | 100 | EA | 1300
97 | SWR11269 | 13 | Fixing of Side Arm along with Cross Arm including angle strut up to 5 feet 11KV | Civil work | Civil work | As per relevent standard specification | 455 | EA | 5915
98 | SWR10671 | 6 | 'T' Branche Erection of Assemble Kit for 'T' Branche | Civil work | Civil work | As per relevent standard specification | 1800 | EA | 10800
99 | SWR21914 | 12 | Erection of Insulated Connectors with covers | Erection work | Erection of work | As per relevent standard specification | 80 | EA | 960
100 | SMR25160 | 12 | S-Insulating Piercing Connector | Supply work | Supply of work | As per relevent standard specification | 1050 | EA | 12600
101 | SWR12125 | 70 | Running of GI eartn flat of size 25X3mm from all metallic parts of channels, AB Switch, HG fuse set,DTr neutral and LT Distribution box and inter connection of earth pits etc complete | 70 |  | As per relevent standard specification | 14.03 | M | 982.1
102 | SMR11486 | 22 | Supply of earthing pipe with materials Supply of GI wire No 8 | Supply work | Supply of work | As per relevent standard specification | 105 | KG | 2310
103 | SWR11039 | 24 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders)0.76 M x 0.76M x 1.83M (2.6" x 2.6" x 6.0") | Civil work | Civil work | As per relevent standard specification | 928 | EA | 22272
104 | SWR20307 | 7 | Sub-transport of poles upto Workspot upto 10KM (Including loading and unloading)8 Mtrs long PSCC Poles | Erection work | Erection of work | As per relevent standard specification | 271.52 | EA | 1900.64
105 | SWR10642 | 8 | Fabrication of 175x85/150x75mm RS joist pieces upto 12.5 meters length by welding joint together by means of 50x6mm flat and MS channel on either side including the cost of consumable. | Fabrication work | Fabrication of work | As per relevent standard specification | 512.55 | EA | 4100.4
106 | SWR10204 | 10 | LOADING of LINE MATERIALS R.S. Joists 175 x 85 mm | LOADING work | LOADING of work | As per relevent standard specification | 76 | EA | 760
107 | SWR10522 | 10 | UNLOADING of LINE MATERIALS R.S. Joists 175 x 85 mm | UNLOADING work | UNLOADING of work | As per relevent standard specification | 50 | EA | 500
108 | SWR10106 | 7 | Excavation of pits in all soils except hard rock requiring blasting 0.6 M x 0.9 M x 1.5 M | Civil work | Civil work | As per relevent standard specification | 645 | EA | 4515
109 | SWR11040 | 8 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders 0.75 M x 0.9 M x 1.95 M | Civil work | Civil work | As per relevent standard specification | 990.68 | EA | 7925.44
110 | SWR11266 | 8 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports,back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation Box pole 9/10/11 Mtr | Erection work | Erection of work | As per relevent standard specification | 2643.83 | EA | 21150.64
111 | SWR21590 | 7 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports,back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation 8.0 m long PSCC poles for Strut | Erection work | Erection of work | As per relevent standard specification | 1500 | EA | 10500
112 | SWR10640 | 5 | Painting of R.S Joist,Box poles including cross arms and clamps with one coat of red oxid and two coats of Al.paint including cost of paint and consumables | Erection work | Erection of work | As per relevent standard specification | 1132 | EA | 5660
113 | SWR11974 | 290 | Laying of XLPE UG cable Double Run including excavation of trench of size 600mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV from road level and cable separation with machine cut bricks horizontally for every 3meters , providing of DWC/GI pipes wherever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth,levelling and removing the debris from the site inluding the cost of lead and lift etc.. (Second cable laying cost not Included) depth of the trench LT-0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs.11 KV 3x185 Sqmm Cable | Erection work | Erection of work | As per relevent standard specification | 631.06 | M | 183007.4
114 | SWR12006 | 60 | Raising of double run cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe)11 KV 3x185 Sqmm Cable | Erection work | Erection of work | As per relevent standard specification | 243.53 | M | 14611.8
115 | SWR10365 | 1.8 | Paving out and stringing of conductor by providing temporary stays, tensioning, sagging correctly, fixing strain points, transferring to pin points binding, keeping stifner, rectification of poles, guys and jumpering etc., including transport of material from road side to location.55 Sqmm Single Circuit (3 Conductors) | Erection work | Erection of work | As per relevent standard specification | 9454.81 | KM | 17018.658
116 | SWR10393 | 2 | Erection of AB Switch and aligment complete Erection of 11KV 400/200A Conventional type AB Switch including fixing of cross angles and alignment complete | Erection work | Erection of work | As per relevent standard specification | 3200 | EA | 6400
117 | SWR10108 | 45 | Excavation of pits in all soils except hard rock requiring blasting 0.75 M x 0.9 M x 1.95 M (1.31 cum) | Civil work | Civil work | As per relevent standard specification | 629.85 | EA | 28343.25
118 | SMR11487 | 100 | Supply of earthing pipe with materials Supply of MS bolts & nuts and washers etc of all sizes | Supply work | Supply of work | As per relevent standard specification | 91.25 | KG | 9125
119 | SWR11180 | 45 | Sub-transport of poles upto Workspot upto 10KM (Including loading and unloading)11 Mtrs long PSCC Poles | Supply work | Supply of work | As per relevent standard specification | 431.97 | EA | 19438.65
120 | SWR34252 | 10 | S&R 25x6mm GI Strip for Earthing | Supply work | Supply of work | As per relevent standard specification | 113 | M | 1130
121 | SWR10978 | 45 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports,back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation 11 Mtrs PSCC poles | Erection work | Erection of work | As per relevent standard specification | 4336.85 | EA | 195158.25
122 | SWR23200 | 1000 | Cut-Tree Branch(LT/11/33)&Trnsprt Debris | Erection work | Erection of work | As per relevent standard specification | 4 | EA | 4000
123 | SMR11482 | 4 | Supply of earthing pipe with materials iii)Supply of CI earth pipe 100 mm dia, 2.75 mt long thickness 10mm with flange as per specication | Supply work | Supply of work | As per relevent standard specification | 3486 | EA | 13944
124 | SWR10357 | 4 | Providing of earthing with excavation of earth pit (0.6x0.6x2.4 Mts.) duly filling with bentonite, earth ,running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.6M dia x 0.5 M height . | Erection work | Erection of work | As per relevent standard specification | 1234.2 | EA | 4936.8
125 | SWR10390 | 8 | Making of Outdoor/Indoor End Termination 11 KV 3x185 Sqmm Cable | Erection work | Erection of work | As per relevent standard specification | 2370.63 | EA | 18965.04
126 | SWR11313 | 0.8 | Restring-LT 3-Ph 34Sqmm-4 Conduct | Erection work | Erection of work | As per relevent standard specification | 7270 | KM | 5816
127 | SWR11308 | 0.8 | Restringing of existing loose Lines by removing the pin-binding and jumpers,Providing of temporary stays, providing stiffners pieces, replacement of damaged insulators, alignment of cross arms, pin binding and jumpering after tensioning and removing of the temporary stays complete .Restringing of with 55 Sqmm single ckt 3 cond | Erection work | Erection of work | As per relevent standard specification | 6616 | KM | 5292.8
128 | SWR10390 | 8 | Making of Outdoor/Indoor End Termination 11 KV 3x185 Sqmm Cable | Erection work | Erection of work | As per relevent standard specification | 2370.63 | EA | 18965.04
129 | SWR11320 | 2 | Dismantling of Damaged Poles, not required and available in the middle of roads, transporting to stock point etc.Dism of 9.1M PSCC Pole | Dismantling work | Dismantling of work | As per relevent standard specification | 948.09 | EA | 1896.18
130 | SWR11324 | 2 | Dismantling of Damaged Poles, not required and available in the middle of roads, transporting to stock point etc Dism of RS Joists 175 x 85 mm | Dismantling work | Dismantling of work | As per relevent standard specification | 1116 | EA | 2232
131 | SWR22065 | 0.2 | LT lines : Dismantling of 11kV 34/ 55 Sqmm SC | Dismantling work | Dismantling of work | As per relevent standard specification | 4500 | KM | 900
132 | SWR11974 | 160 | Laying of XLPE UG cable Double Run including excavation of trench of size 600mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV from road level and cable separation with machine cut bricks horizontally for every 3 meters , providing of DWC/GI pipes wherever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth,levelling and removing the debris from the site inluding the cost of lead and lift etc.. (Second cable laying cost not Included) depth of the trench LT-0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs.11 KV 3x185 Sqmm Cable | Erection work | Erection of work | As per relevent standard specification | 631.06 | M | 100969.6
133 | SWR12006 | 40 | Raising of double run cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe)-11 KV 3x185 Sqmm Cable | Erection work | Erection of work | As per relevent standard specification | 243.53 | M | 9741.2
134 | SWR20863 | 2 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports,back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation Erection of 5 Mts RS Joist (Bit) Pole including fixing of Pole Mounted Box | Erection work | Erection of work | As per relevent standard specification | 1044.23 | EA | 2088.46
135 | SWR10988 | 160 | Laying of the cable along the footpath through 225mm dia GI pipe for 33KV, 150mm dia GI pipe for 11KV (excluding the cost of GI pipe)Laying of 2nd cable in excavated trench | Erection work | Erection of work | As per relevent standard specification | 204.1 | M | 32656
2010106